## APR ANX I Signed copy (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [18 empty] | 2014-04-01 | 30 | 30
Annexure -I Form-I | [18 empty] | 2014-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR APRIL-16 OF FY 2016-17 | [18 empty] | 2014-06-01 | 30 | 30
[19 empty] | 2014-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for April-2016 |  |  |  | Reliability for cummulative period From April-16 | [5 empty] | 2014-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  | 2014-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  | 2014-10-01 | 31 | 31
1 | Davangere | 33 | 31 | 1.05 | 1.05 | 193.64 | 33.54 | 227.18 | 228.23 | 6.9161 | 99.0439 | 99.0394 | 228.23 | 6.9161 | 99.0439 | 99.0394 | 0 | 0 | 2014-11-01 | 30 | 30
2 | Chitradurga | 11 | 11 | 1.5 | 1.5 | 203.9 | 157.7 | 361.6 | 363.1 | 33.0091 | 95.4343 | 95.4154 | 363.1 | 33.0091 | 95.4343 | 95.4154 | 0 | 0 | 2014-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 15 | 15 | 367 | 190 | 557 | 572 | 19.0667 | 97.4213 | 97.3519 | 572 | 19.0667 | 97.4213 | 97.3519 | 0 | 0 | 2014-01-01 | 31 | 31
4 | Bangalore Urban | 1312 | 1144 | 400.54 | 400.54 | 14669.53 | 4754.11 | 19423.64 | 19824.18 | 15.1099 | 97.9438 | 97.9014 | 19824.18 | 15.1099 | 97.9438 | 97.9014 | 0 | 0 | 2014-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 13.08 | 13.08 | 21.95 | 21.75 | 43.7 | 56.78 | 14.195 | 98.4826 | 98.0285 | 56.78 | 14.195 | 98.4826 | 98.0285 | 0 | 0 | 2014-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 13.59 | 13.59 | 64.08 | 50.2 | 114.28 | 127.87 | 10.6558 | 98.6773 | 98.52 | 127.87 | 10.6558 | 98.6773 | 98.52 | 0 | 0 |  | 366 | 0
7 | CBPura | 12 | 12 | 12.2 | 12.2 | 90.32 | 46.17 | 136.49 | 148.69 | 12.3908 | 98.4203 | 98.2791 | 148.69 | 12.3908 | 98.4203 | 98.2791 | 0 | 0
Assistant Executive Engineer(Ele) | [13 empty] | Deputy General Manager(Ele)
Operation-1 | [13 empty] | Operation-2
Chief General Manager(Ele)
Operation

## APR ANXIII DIVISION (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR APRIL-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Apr-2016 |  |  |  | Reliability for cummulative period From Apilr-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 227 | 224 | 159.12 | 159.12 | 2968.9697 | 2355.46 | 5324.4297 | 5483.5497 | 24.1566 | 95.6564 | 95.5266 | 5483.5497 | 24.1566 | 95.6564 | 95.5266
2 | Harihara | 152 | 152 | 153.2 | 153.2 | 2388.04 | 1819.116 | 4207.156 | 4360.356 | 28.6866 | 94.8743 | 94.6877 | 4360.356 | 28.6866 | 94.8743 | 94.6877
3 | Chitradurga | 178 | 178 | 125.13 | 125.13 | 3383.18 | 3735.09 | 7118.27 | 7243.4 | 40.6933 | 92.5944 | 92.4642 | 7243.4 | 40.6933 | 92.5944 | 92.4642
4 | Hiriyur | 185 | 185 | 42.04 | 42.04 | 1829.58 | 785.98 | 2615.56 | 2657.6 | 14.3654 | 97.3818 | 97.3397 | 2657.6 | 14.3654 | 97.3818 | 97.3397
5 | Tumkur | 332 | 332 | 121.4 | 121.4 | 3917 | 4514 | 8431 | 8552.4 | 25.7602 | 95.2973 | 95.2296 | 8552.4 | 25.7602 | 95.2973 | 95.2296
6 | Tiptur | 187 | 187 | 126.3 | 126.3 | 2206 | 3689 | 5895 | 6021.3 | 32.1995 | 94.1622 | 94.0371 | 6021.3 | 32.1995 | 94.1622 | 94.0371
7 | Madhugiri | 257 | 257 | 38.5 | 38.5 | 3312 | 2878 | 6190 | 6228.5 | 24.2354 | 95.5397 | 95.512 | 6228.5 | 24.2354 | 95.5397 | 95.512
8 | Kolar | 134 | 134 | 25.46 | 25.46 | 731.34 | 498.48 | 1229.82 | 1255.28 | 9.3678 | 98.3004 | 98.2652 | 1255.28 | 9.3678 | 98.3004 | 98.2652
9 | KGF | 161 | 161 | 49.35 | 49.35 | 497.3 | 159 | 656.3 | 705.65 | 4.3829 | 99.2451 | 99.1883 | 705.65 | 4.3829 | 99.2451 | 99.1883
10 | CB Pura | 172 | 172 | 83.03 | 83.03 | 346.04 | 257.38 | 603.42 | 686.45 | 3.991 | 99.3503 | 99.2609 | 686.45 | 3.991 | 99.3503 | 99.2609
11 | Chintamani | 120 | 120 | 96.13 | 96.13 | 694.15 | 539.1 | 1233.25 | 1329.38 | 11.0782 | 98.0968 | 97.9485 | 1329.38 | 11.0782 | 98.0968 | 97.9485
12 | Devanahalli | 32 | 32 | 15.6 | 15.6 | 325.6167 | 1833.2 | 2158.8167 | 2174.4167 | 67.9505 | 87.5068 | 87.4166 | 2174.4167 | 67.9505 | 87.5068 | 87.4166
13 | Hosakote | 32 | 32 | 55.74 | 55.74 | 269.93 | 758.48 | 1028.41 | 1084.15 | 33.8797 | 94.0486 | 93.726 | 1084.15 | 33.8797 | 94.0486 | 93.726
12 | Yelahanaka | 64 | 64 | 71.34 | 71.34 | 595.5467 | 2591.68 | 3187.2267 | 3258.5667 | 50.9151 | 90.7777 | 90.5713 | 3258.5667 | 50.9151 | 90.7777 | 90.5713
14 | Nelamangala | 14 | 14 | 12.61 | 12.61 | 116.73 | 184.71 | 301.44 | 314.05 | 22.4321 | 96.0127 | 95.8459 | 314.05 | 22.4321 | 96.0127 | 95.8459
15 | Doddaballapura | 35 | 35 | 27.7 | 27.7 | 111.25 | 546.6 | 657.85 | 685.55 | 19.5871 | 96.5193 | 96.3728 | 685.55 | 19.5871 | 96.5193 | 96.3728
16 | Magadi | 40 | 40 | 26.1 | 26.1 | 249.05 | 349.95 | 599 | 625.1 | 15.6275 | 97.2269 | 97.106 | 625.1 | 15.6275 | 97.2269 | 97.106
13 | Nelamanagala | 89 | 89 | 66.41 | 66.41 | 477.03 | 1081.26 | 1558.29 | 1624.7 | 18.2551 | 96.7576 | 96.6194 | 1624.7 | 18.2551 | 96.7576 | 96.6194
14 | Chandapura | 19 | 19 | 0.51042 | 0.51042 | 23.9854 | 4.4854 | 28.4708 | 28.9812 | 1.5253 | 99.7225 | 99.7175 | 28.9812 | 1.5253 | 99.7225 | 99.7175
18 | Ramanagara | 34 | 34 | 56.59 | 56.59 | 62.51 | 11.54 | 74.05 | 130.64 | 3.8424 | 99.5967 | 99.2885 | 130.64 | 3.8424 | 99.5967 | 99.2885
19 | Channapatna | 47 | 47 | 21.41 | 21.41 | 269.3221 | 162.934 | 432.2561 | 453.6661 | 9.6525 | 98.2969 | 98.2125 | 453.6661 | 9.6525 | 98.2969 | 98.2125
15 | Ramanagara | 81 | 81 | 78 | 78 | 331.8321 | 174.474 | 506.3061 | 584.3061 | 7.2137 | 98.8425 | 98.6641 | 584.3061 | 7.2137 | 98.8425 | 98.6641
16 | Kanakapura | 64 | 64 | 0.11597 | 0.11597 | 41.6931 | 36.7646 | 78.4576 | 78.5736 | 1.2277 | 99.773 | 99.7726 | 78.5736 | 1.2277 | 99.773 | 99.7726
Note: 1. Devanahalli and Hoskote subdivisions are clubed under Yelahanaka Division.
2. Nelamangala, Doddaballapura and Magadi subdivisions are clubed under Nelamanagala Division.
3. Details under Anekal subdivision peratins to Chandapura Division.
4. Ramnagara and channaptana subdivisions are clubed under Ramnagara Division.

## MAY ANX I Signed copy (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [18 empty] | 2014-04-01 | 30 | 30
Annexure -I Form-I | [18 empty] | 2014-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR MAY-16 OF FY 2016-17 | [18 empty] | 2014-06-01 | 30 | 30
[19 empty] | 2014-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for MAY-2016 |  |  |  | Reliability for cummulative period From April-16 | [5 empty] | 2014-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  | 2014-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  | 2014-10-01 | 31 | 31
1 | Davangere | 33 | 31 | 0 | 1.05 | 577.01 | 406.46 | 983.47 | 983.47 | 29.8021 | 95.9943 | 95.9943 | 1211.7 | 36.7182 | 97.4919 | 97.4919 | -1.4976 | -1.4976 | 2014-11-01 | 30 | 30
2 | Chitradurga | 11 | 11 | 6.2 | 7.7 | 198.93 | 154.92 | 353.85 | 360.05 | 32.7318 | 95.6763 | 95.6006 | 723.15 | 65.7409 | 95.548 | 95.5095 | 0.12832 | 0.091061 | 2014-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 18 | 33 | 328 | 201 | 529 | 547 | 18.2333 | 97.6299 | 97.5493 | 1119 | 37.3 | 97.4932 | 97.4522 | 0.13676 | 0.097097 | 2014-01-01 | 31 | 31
4 | Bangalore Urban | 1321 | 1142 | 703.34 | 1103.88 | 7112.12 | 6351.5 | 13463.62 | 14166.96 | 10.7244 | 98.6301 | 98.5585 | 33991.14 | 25.7314 | 98.2788 | 98.2424 | 0.35135 | 0.31615 | 2014-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 12.08 | 25.16 | 6.8479 | 7.6354 | 14.4833 | 26.5633 | 6.6408 | 99.5133 | 99.1074 | 83.3433 | 20.8358 | 98.7831 | 98.5768 | 0.73026 | 0.53063 | 2014-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 8.38 | 21.97 | 44.58 | 22.24 | 66.82 | 75.2 | 6.2667 | 99.2516 | 99.1577 | 203.07 | 16.9225 | 98.8918 | 98.8441 | 0.83727 | 0.33746 |  | 366 | 0
7 | CBPura | 9 | 9 | 68.05 | 80.25 | 24.28 | 15.37 | 39.65 | 107.7 | 11.9667 | 99.4079 | 98.3916 | 256.39 | 28.4878 | 98.5706 | 98.0541 | 0.83727 | 0.33746
Assistant Executive Engineer(Ele) | [13 empty] | Deputy General Manager(Ele)
Operation-1 | [13 empty] | Operation-2
Chief General Manager(Ele)
Operation

## MAY ANXII ref (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR MAY-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for MAY-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 11.5 | #REF! | 27.5 | 9.6 | 37.1 | 48.6 | 48.6 | 95.0134 | 93.4677 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 21 | #REF! | 20.35 | 0.5 | 20.85 | 41.85 | 41.85 | 97.1976 | 94.375 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 17 | 17 | 46.36 | #REF! | 327.55 | 533.15 | 860.7 | 907.06 | 53.3565 | 93.195 | 92.8284 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 3 | 3 | 39.45 | #REF! | 130.2 | 37.5 | 167.7 | 207.15 | 69.05 | 92.4866 | 90.7191 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 9 | 9 | 24.3 | #REF! | 172.2 | 88.5 | 260.7 | 285 | 31.6667 | 96.1066 | 95.7437 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 2.5 | #REF! | 20.55 | 12.66 | 33.21 | 35.71 | 35.71 | 95.5363 | 95.2003 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 4.5 | #REF! | 44.9 | 37.75 | 82.65 | 87.15 | 43.575 | 94.4456 | 94.1431 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 8.3537 | #REF! | 21.1 | 6.15 | 27.25 | 35.6037 | 11.8679 | 98.7791 | 98.4048 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 9.6862 | #REF! | 9.58 | 6.45 | 16.03 | 25.7163 | 5.1433 | 99.5691 | 99.3087 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 0.56375 | #REF! | 4.35 | 1.05 | 5.4 | 5.9637 | 5.9637 | 99.2742 | 99.1984 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 18 | #REF! | 256 | 125 | 381 | 399 | 57 | 92.6843 | 92.3387 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 15 | #REF! | 198 | 141 | 339 | 354 | 32.1818 | 95.8578 | 95.6745 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 10 | 10 | 14 | #REF! | 295 | 105 | 400 | 414 | 41.4 | 94.6237 | 94.4355 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.43 | #REF! | 24.43 | 18.11 | 42.54 | 43.97 | 10.9925 | 98.5706 | 98.5225 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 71 | #REF! | 94.3 | 53 | 147.3 | 218.3 | 7.2767 | 99.3401 | 99.022 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 58.45 | #REF! | 63.24 | 43.08 | 106.32 | 164.77 | 10.9847 | 99.0473 | 98.5236 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 10.35 | #REF! | 78.33 | 58.11 | 136.44 | 146.79 | 12.2325 | 98.4718 | 98.3558 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 34.4 | #REF! | 13.45 | 14.7167 | 28.1667 | 62.5667 | 1.2769 | 99.9227 | 99.8284 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 60 | 60 | 56.3985 | #REF! | 379.4104 | 365.2253 | 744.6357 | 801.0342 | 13.3506 | 98.3319 | 98.2056 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 14.22 | #REF! | 885.99 | 1428.05 | 2314.04 | 2328.26 | 48.5054 | 93.5203 | 93.4805 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 15.3 | #REF! | 382.9 | 604.3 | 987.2 | 1002.5 | 27.8472 | 96.3142 | 96.2571 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 24 | 24 | 28.79 | #REF! | 275.19 | 618.96 | 894.15 | 922.94 | 38.4558 | 94.9924 | 94.8312 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 85.6146 | #REF! | 85.6146 | 75.2674 | 160.8819 | 246.4965 | 1.9409 | 99.8297 | 99.7391 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 45.12 | #REF! | 15.6035 | 7.4875 | 23.091 | 68.211 | 2.8421 | 99.8707 | 99.618 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 14.64 | #REF! | 3.0578 | 2.8319 | 5.8897 | 20.5297 | 2.9328 | 99.8869 | 99.6058 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 1.08 | #REF! | 6.6396 | 6.266 | 12.9056 | 13.9856 | 0.63571 | 99.9212 | 99.9146 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
|  | 529 | 529 | 652.0068 | #REF! | 3835.4358 | 4399.7147 | 8235.1506 | 8887.1574 | 656.6387 | 97.8379 | 97.6667 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
20000
5000
5000
8000
18000
2000
[11 empty] | 2522.789 | 2511.7421 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 97.0303 | 96.6055 |  |  | #REF! | #REF!

## June ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR June-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for June-2016 |  |  |  | Reliability for cummulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 33 | 30 | 22.43 | #REF! | 373 | 115.75 | 488.75 | 511.18 | 15.4903 | 97.943 | 97.8486 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30
2 | Chitradurga | 11 | 11 | 5.5 | #REF! | 199.2 | 154.5 | 353.7 | 359.2 | 32.6545 | 95.5341 | 95.4646 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 10 | #REF! | 256 | 188 | 444 | 454 | 15.1333 | 97.9444 | 97.8981 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1321 | 1130 | 431.45 | #REF! | 5461.36 | 4875.59 | 10336.95 | 10768.4 | 8.1517 | 98.9132 | 98.8678 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 1.4 | #REF! | 35.32 | 21.01 | 56.33 | 57.73 | 14.4325 | 98.0441 | 97.9955 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 8.54 | #REF! | 70.46 | 64.93 | 135.39 | 143.93 | 11.9942 | 98.433 | 98.3341 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 10.2 | #REF! | 33.55 | 26.05 | 59.6 | 69.8 | 7.7556 | 99.0802 | 98.9228 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1417 | 1223 | 491.18 | #REF! | 6391.98 | 5406.95 | 11798.93 | 12290.11 | 101.3735 | 98.8435 | 98.6043 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
686.1
98.0143

## June ANXII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR June-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for June-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 1.2 | #REF! | 25.6 | 4.7 | 30.3 | 31.5 | 31.5 | 95.7917 | 95.625 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 9.1 | #REF! | 21.55 | 2.2 | 23.75 | 32.85 | 32.85 | 96.7014 | 95.4375 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 33.12 | #REF! | 74.35 | 88.25 | 162.6 | 195.72 | 17.7927 | 97.947 | 97.5288 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 12.25 | #REF! | 54 | 15.35 | 69.35 | 81.6 | 40.8 | 95.184 | 94.3333 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 6.2 | #REF! | 41.45 | 57.4 | 98.85 | 105.05 | 26.2625 | 96.5677 | 96.3524 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 4.2 | #REF! | 20.57 | 12.62 | 33.19 | 37.39 | 37.39 | 95.3903 | 94.8069 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 6.2 | #REF! | 44.95 | 37.67 | 82.62 | 88.82 | 44.41 | 94.2625 | 93.8319 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 8.5626 | #REF! | 20.9 | 5.95 | 26.85 | 35.4126 | 11.8042 | 98.7569 | 98.3605 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 9.9284 | #REF! | 9.38 | 6.25 | 15.63 | 25.5584 | 5.1117 | 99.5658 | 99.29 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 0.57784 | #REF! | 4.15 | 0.85 | 5 | 5.5778 | 5.5778 | 99.3056 | 99.2253 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 14 | #REF! | 324 | 80 | 404 | 418 | 59.7143 | 91.9841 | 91.7063 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 15 | #REF! | 594 | 423 | 1017 | 1032 | 93.8182 | 87.1591 | 86.9697 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 10 | 10 | 5.47 | #REF! | 239.4 | 169.67 | 409.07 | 414.54 | 41.454 | 94.3185 | 94.2425 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.66 | #REF! | 26.34 | 17.91 | 44.25 | 45.91 | 11.4775 | 98.4635 | 98.4059 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 96 | #REF! | 85 | 63.05 | 148.05 | 244.05 | 8.135 | 99.3146 | 98.8701 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 15.2 | #REF! | 53.27 | 45 | 98.27 | 113.47 | 7.5647 | 99.0901 | 98.9494 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 14.55 | #REF! | 23.3 | 20.43 | 43.73 | 58.28 | 4.8567 | 99.4939 | 99.3255 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 33.95 | #REF! | 1050.9167 | 2861.2 | 3912.1167 | 3946.0667 | 80.532 | 88.9112 | 88.815 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 84.52 | #REF! | 810.33 | 886.28 | 1696.61 | 1781.13 | 30.1886 | 96.0061 | 95.8071 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 47 | 47 | 1.5 | #REF! | 770.21 | 829.28 | 1599.49 | 1600.99 | 34.0636 | 95.2734 | 95.2689 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 60 | #REF! | 724.85 | 719.15 | 1444 | 1504 | 41.7778 | 94.429 | 94.1975 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 72.75 | #REF! | 224.14 | 115.28 | 339.42 | 412.17 | 15.8527 | 98.1869 | 97.7982 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 111.34 | #REF! | 111.3372 | 43.7139 | 155.0511 | 266.3911 | 2.0976 | 99.8304 | 99.7087 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 3.2 | #REF! | 54.85 | 21.35 | 76.2 | 79.4 | 3.3083 | 99.559 | 99.5405 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 3.55 | #REF! | 48.98 | 14.4389 | 63.4189 | 66.9689 | 9.567 | 98.7417 | 98.6713 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 0.43 | #REF! | 7.2875 | 2.8833 | 10.1708 | 10.6008 | 0.48186 | 99.9358 | 99.9331 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
Note:Reconsiled Figures (feeders feeding to industrial and water supply considered in annexure 2 are shifted to rural feeders in annexure 3 in harihara, honnalli, harapanahalli and in hoskote), Nelamangala each one feeder becom idle.
|  | 517 | 517 | 624.4588 | #REF! | 5465.1114 | 6543.8761 | 12008.9875 | 12633.4463 | 698.3887 | 96.7739 | 96.6061 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
20000
5000
5000
8000
18000
2000
[11 empty] | 2510.1702 | 2503.0016 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 96.545 | 96.2693 |  |  | #REF! | #REF!

## June ANXIII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR June-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for June-2016 |  |  |  | Reliability for cummulative period From Apilr-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 229 | 226 | 297.43 | #REF! | 6394.05 | 7092 | 13486.05 | 13783.48 | 60.1899 | 89.0943 | 88.8537 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 163 | 163 | 125.97 | #REF! | 4949.77 | 8352.05 | 13301.82 | 13427.79 | 82.3791 | 84.8877 | 84.7446 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 151.25 | #REF! | 3306.98 | 3681.66 | 6988.64 | 7139.89 | 40.1117 | 92.7293 | 92.5719 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 190 | 190 | 43.5219 | #REF! | 3442.35 | 2682.57 | 6124.92 | 6168.4419 | 32.4655 | 94.0303 | 93.9879 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 331 | 331 | 156 | #REF! | 2856 | 13895 | 16751 | 16907 | 51.0785 | 90.6283 | 90.541 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6
6 | Tiptur | 187 | 187 | 120 | #REF! | 2345 | 6425 | 8770 | 8890 | 47.5401 | 91.3151 | 91.1963 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2
7 | Madhugiri | 270 | 270 | 256 | #REF! | 2985 | 5234 | 8219 | 8475 | 31.3889 | 94.3628 | 94.1872 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2667
8 | Kolar | 134 | 134 | 33.42 | #REF! | 436.58 | 236.68 | 673.26 | 706.68 | 5.2737 | 99.0696 | 99.0234 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 161 | 161 | 234 | #REF! | 122 | 99 | 221 | 455 | 2.8261 | 99.7458 | 99.4767 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.9
10 | CB Pura | 172 | 172 | 363.3 | #REF! | 427.54 | 356.35 | 783.89 | 1147.19 | 6.6697 | 99.156 | 98.7649 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 6.055
11 | Chintamani | 120 | 120 | 64.25 | #REF! | 434.5 | 336.4 | 770.9 | 835.15 | 6.9596 | 98.8103 | 98.7112 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 32 | 32 | 10.05 | #REF! | 573.95 | 743.27 | 1317.22 | 1327.27 | 41.4772 | 92.3772 | 92.319 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 32 | 32 | 40.48 | #REF! | 365.77 | 639.43 | 1005.2 | 1045.68 | 32.6775 | 94.1829 | 93.9486 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 64 | 64 | 50.53 | #REF! | 939.72 | 1382.7 | 2322.42 | 2372.95 | 37.0773 | 93.28 | 93.1338 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 0.7 | #REF! | 156.69 | 320.1 | 476.79 | 477.49 | 34.1064 | 93.6933 | 93.684 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 73.7 | #REF! | 2652.605 | 1576.15 | 4228.755 | 4302.455 | 122.9273 | 77.6256 | 77.2357 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 107.85 | #REF! | 411.95 | 621.24 | 1033.19 | 1141.04 | 28.526 | 95.2167 | 94.7174 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 182.25 | #REF! | 3221.245 | 2517.49 | 5738.735 | 5920.985 | 66.5279 | 88.0592 | 87.68 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.47 | #REF! | 6.7 | 4.4854 | 11.1854 | 11.6554 | 0.61344 | 99.891 | 99.8864 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 15.57 | #REF! | 29.799 | 13.3569 | 43.156 | 58.726 | 1.7272 | 99.7649 | 99.6801 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 10.19 | #REF! | 126.8047 | 91.8896 | 218.6943 | 228.8843 | 4.8699 | 99.1383 | 99.0982 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 25.76 | #REF! | 163.3037 | 109.7319 | 261.8503 | 287.6103 | 3.5507 | 99.4013 | 99.3425 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 1.73 | #REF! | 57.5639 | 57.5528 | 115.1167 | 116.8467 | 1.8257 | 99.6669 | 99.6619 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 2155 | 2152 | 2043.68 | #REF! | 24706.7714 | 41751.8267 | 66447.4126 | 68491.0926 | 587.8332 | 95.7115 | 95.5796 | #REF! | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
0
0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1885.3863 | 1882.2901
|  | 2452 | [8 empty] | 94.2693 | 94.1145
[15 empty] | #REF! | #REF!
2452
|  | 1420 | [7 empty] | 5630.95 |  |  |  |  | #REF! | #REF!
529
4401
138.87

## July ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR JULY-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for July-2016 |  |  |  | Reliability for cummulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 0 | #REF! | 300.43 | 87.27 | 387.7 | 387.7 | 11.4029 | 98.4673 | 98.4673 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30
2 | Chitradurga | 11 | 11 | 5.8 | #REF! | 198.7 | 149.53 | 348.23 | 354.03 | 32.1845 | 95.745 | 95.6741 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 15 | #REF! | 235 | 196 | 431 | 446 | 14.8667 | 98.069 | 98.0018 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1323 | 1082 | 439.08 | #REF! | 3811.56 | 4901.19 | 8712.75 | 9151.83 | 6.9175 | 99.1148 | 99.0702 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 1.35 | #REF! | 29.32 | 14.01 | 43.33 | 44.68 | 11.17 | 98.544 | 98.4987 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 1.8 | #REF! | 100.03 | 54.79 | 154.82 | 156.62 | 13.0517 | 98.2659 | 98.2457 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 11.3 | #REF! | 42.1 | 33.05 | 75.15 | 86.45 | 9.6056 | 98.8777 | 98.7089 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1420 | 1176 | 483.83 | #REF! | 4659.21 | 5414.1 | 10073.31 | 10557.14 | 95.7527 | 99.0147 | 98.7532 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
98.1548
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
686.1
98.0143

## July ANXII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR July-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for July-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 2.15 | #REF! | 15.3 | 2.3 | 17.6 | 19.75 | 19.75 | 97.6344 | 97.3454 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 0 | #REF! | 20.2 | 0.5 | 20.7 | 20.7 | 20.7 | 97.2177 | 97.2177 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 5.4 | #REF! | 50.32 | 22.2 | 72.52 | 77.92 | 7.0836 | 99.1139 | 99.0479 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 5.4 | #REF! | 73.35 | 15 | 88.35 | 93.75 | 46.875 | 94.0625 | 93.6996 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 2.5 | #REF! | 25.3 | 3.3 | 28.6 | 31.1 | 7.775 | 99.039 | 98.955 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 4.5 | #REF! | 20.53 | 12.17 | 32.7 | 37.2 | 37.2 | 95.6048 | 95 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 6.5 | #REF! | 44.85 | 36.77 | 81.62 | 88.12 | 44.06 | 94.5148 | 94.078 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 10.9708 | #REF! | 47.67 | 18.15 | 65.82 | 76.7908 | 25.5969 | 97.0511 | 96.5596 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 12.7208 | #REF! | 19.45 | 40.37 | 59.82 | 72.5408 | 14.5082 | 98.3919 | 98.05 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 1.7404 | #REF! | 17.45 | 5.05 | 22.5 | 24.2404 | 24.2404 | 96.9758 | 96.7419 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 13 | #REF! | 324 | 80 | 404 | 417 | 59.5714 | 92.2427 | 91.9931 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 14 | #REF! | 594 | 423 | 1017 | 1031 | 93.7273 | 87.5733 | 87.4022 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 0.25 | #REF! | 177.9 | 100.75 | 278.65 | 278.9 | 34.8625 | 95.3184 | 95.3142 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.62 | #REF! | 27.41 | 25.7 | 53.11 | 54.73 | 13.6825 | 98.2154 | 98.161 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 132 | #REF! | 78 | 71 | 149 | 281 | 9.3667 | 99.3324 | 98.741 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 6.1 | #REF! | 83.27 | 65.57 | 148.84 | 154.94 | 10.3293 | 98.6663 | 98.6116 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 21 | #REF! | 63.56 | 45.05 | 108.61 | 129.61 | 10.8008 | 98.7835 | 98.5483 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 19.35 | #REF! | 1944.0833 | 2201.5667 | 4145.65 | 4165 | 85 | 88.6283 | 88.5753 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 111.99 | #REF! | 2903.9233 | 3385.2867 | 6289.21 | 6401.2 | 108.4949 | 85.6725 | 85.4174 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 33.21 | #REF! | 758.9 | 964.31 | 1723.21 | 1756.42 | 36.5921 | 95.1747 | 95.0817 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 22.5 | #REF! | 519.69 | 1099.3 | 1618.99 | 1641.49 | 45.5969 | 93.9554 | 93.8714 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 80.15 | #REF! | 363.45 | 143.42 | 506.87 | 587.02 | 22.5777 | 97.3797 | 96.9654 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 65.3944 | #REF! | 65.3944 | 45.8625 | 111.2569 | 176.6514 | 1.391 | 99.8823 | 99.813 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 11.33 | #REF! | 61.28 | 26.24 | 87.52 | 98.85 | 4.1188 | 99.5099 | 99.4464 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 11.48 | #REF! | 684.8535 | 60.9217 | 745.7751 | 757.2551 | 108.1793 | 85.6802 | 85.4598 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 0.32639 | #REF! | 8.5188 | 2.4243 | 10.9431 | 11.2694 | 0.51225 | 99.9331 | 99.9311 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
Note: The Madhugiri 2 Nos of feeders reduced due to Kodigenahalli & Y N Hoskote of Madhugiri otwn are rural areas and considered under annexure-3
|  | 516 | 516 | 595.5828 | #REF! | 8992.6533 | 8896.2118 | 17888.8651 | 18484.4479 | 892.5925 | 95.185 | 95.0246 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
20000
5000
5000
8000
18000
2000
[11 empty] | 2485.554 | 2480.0279 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 95.5982 | 95.3857 |  |  | #REF! | #REF!

## July ANXIII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR July-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for July-2016 |  |  |  | Reliability for cummulative period From Apilr-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 229 | 226 | 79.15 | #REF! | 5374.11 | 4260.69 | 9634.8 | 9713.95 | 42.419 | 92.46 | 92.398 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 163 | 163 | 34.58 | #REF! | 4268.73 | 3929.74 | 8198.47 | 8233.05 | 50.5095 | 90.9861 | 90.9481 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 148.5 | #REF! | 3298.86 | 3601.21 | 6900.07 | 7048.57 | 39.5987 | 93.053 | 92.9035 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 190 | 190 | 44.3923 | #REF! | 3165.88 | 2387.48 | 5553.36 | 5597.7523 | 29.4619 | 94.762 | 94.7201 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 349 | 85 | #REF! | 2685 | 12895 | 15580 | 15665 | 40.6883 | 92.7478 | 92.7082 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.4167
6 | Tiptur | 187 | 187 | 105 | #REF! | 2156 | 6523 | 8679 | 8784 | 46.9733 | 91.6825 | 91.5819 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.75
7 | Madhugiri | 272 | 272 | 22.56 | #REF! | 2896 | 5145 | 8041 | 8063.56 | 29.6454 | 94.7021 | 94.6872 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.376
8 | Kolar | 134 | 134 | 35.21 | #REF! | 564.8 | 373.41 | 938.21 | 973.42 | 7.2643 | 98.7452 | 98.6981 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 161 | 161 | 256 | #REF! | 351 | 142 | 493 | 749 | 4.6522 | 99.4512 | 99.1663 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2667
10 | CB Pura | 172 | 172 | 917.3 | #REF! | 327.54 | 179.17 | 506.71 | 1424.01 | 8.2791 | 99.472 | 98.5163 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 15.2883
11 | Chintamani | 120 | 120 | 74.52 | #REF! | 503.4 | 486.6 | 990 | 1064.52 | 8.871 | 98.5215 | 98.4102 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 32 | 32 | 15.5 | #REF! | 839.6 | 1035.5167 | 1875.1167 | 1890.6167 | 59.0818 | 89.4987 | 89.4119 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 32 | 32 | 48.7725 | #REF! | 1256.75 | 1917.6167 | 3174.3667 | 3223.1392 | 100.7231 | 82.2224 | 81.9493 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 64 | 64 | 64.2725 | #REF! | 2096.35 | 2953.1333 | 5049.4833 | 5113.7558 | 79.9024 | 85.8605 | 85.6806 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 17.71 | #REF! | 150.32 | 435.38 | 585.7 | 603.41 | 43.1007 | 92.5026 | 92.2759 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 80.6 | #REF! | 309.25 | 1131.25 | 1440.5 | 1521.1 | 43.46 | 92.6242 | 92.2115 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 174.63 | #REF! | 381.5683 | 543.6 | 925.1683 | 1099.7983 | 27.495 | 95.855 | 95.0726 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 272.94 | #REF! | 841.1383 | 2110.23 | 2951.3683 | 3224.3083 | 36.2282 | 94.0571 | 93.5075 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.47 | #REF! | 6.9 | 4.5 | 11.4 | 11.87 | 0.62474 | 99.8925 | 99.888 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 27.59 | #REF! | 37.3658 | 23.4369 | 60.8028 | 88.3928 | 2.5998 | 99.6795 | 99.5341 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 29.15 | #REF! | 321.5744 | 389.8475 | 711.4219 | 740.5719 | 15.7568 | 97.2873 | 97.1762 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 56.74 | #REF! | 358.9403 | 413.2844 | 772.2247 | 828.9647 | 10.2341 | 98.2915 | 98.1659 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 4.72 | #REF! | 69 | 68 | 137 | 141.72 | 2.2144 | 99.6164 | 99.6032 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 2211 | 2172 | 2367.835 | #REF! | 21526.6072 | 41030.6656 | 62557.2728 | 64925.1078 | 610.2137 | 95.9998 | 95.8484 | #REF! | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
0
0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1895.7619 | 1891.8604
|  | 2508 | [8 empty] | 94.7881 | 94.593
[15 empty] | #REF! | #REF!
2508
|  | 1420 | [7 empty] | 8371.7558 |  |  |  |  | #REF! | #REF!
529
4457
138.87

## Aug ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Aug-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Aug-2016 |  |  |  | Reliability for cummulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 2.18 | #REF! | 251.55 | 51.05 | 302.6 | 304.78 | 8.9641 | 98.8038 | 98.7951 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153 | 183
2 | Chitradurga | 11 | 11 | 4.2 | #REF! | 201.34 | 135.61 | 336.95 | 341.15 | 31.0136 | 95.8828 | 95.8315 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 10 | #REF! | 210 | 180 | 390 | 400 | 13.3333 | 98.2527 | 98.2079 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1335 | 1089 | 898.54 | #REF! | 3913.17 | 3645.13 | 7558.3 | 8456.84 | 6.3347 | 99.239 | 99.1486 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 22.28 | #REF! | 35.53 | 32.87 | 68.4 | 90.68 | 22.67 | 97.7016 | 96.953 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 1 | #REF! | 110.3 | 30.4 | 140.7 | 141.7 | 11.8083 | 98.4241 | 98.4129 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 21.15 | #REF! | 54.1 | 49.2 | 103.3 | 124.45 | 13.8278 | 98.4573 | 98.1414 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1432 | 1183 | 979.5 | #REF! | 4719.79 | 4143.06 | 8862.85 | 9842.35 | 109.9714 | 99.1404 | 98.8445 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
1435
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
686.1
98.0143

## Aug ANXII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Aug-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Aug-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 2.15 | #REF! | 17.75 | 0.3 | 18.05 | 20.2 | 20.2 | 97.5739 | 97.2849 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 4.5 | #REF! | 24.3 | 0.5 | 24.8 | 29.3 | 29.3 | 96.6667 | 96.0618 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 0.25694 | #REF! | 37.17 | 27.2 | 64.37 | 64.6269 | 5.8752 | 99.2135 | 99.2103 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 0.3 | #REF! | 54.4 | 7.4 | 61.8 | 62.1 | 31.05 | 95.8468 | 95.8266 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 1.2 | #REF! | 11.55 | 1.05 | 12.6 | 13.8 | 3.45 | 99.5766 | 99.5363 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 3.25 | #REF! | 20.77 | 10.91 | 31.68 | 34.93 | 34.93 | 95.7419 | 95.3051 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 5.4 | #REF! | 45.33 | 34.24 | 79.57 | 84.97 | 42.485 | 94.6526 | 94.2897 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 11.2451 | #REF! | 47.67 | 18.15 | 65.82 | 77.0651 | 25.6884 | 97.0511 | 96.5473 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 13.0388 | #REF! | 19.45 | 40.37 | 59.82 | 72.8588 | 14.5718 | 98.3919 | 98.0414 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 1.7839 | #REF! | 17.45 | 5.05 | 22.5 | 24.2839 | 24.2839 | 96.9758 | 96.736 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 8 | #REF! | 299 | 91 | 390 | 398 | 56.8571 | 92.5115 | 92.3579 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 14 | #REF! | 165.65 | 82.15 | 247.8 | 261.8 | 23.8 | 96.9721 | 96.8011 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 7 | #REF! | 160 | 87 | 247 | 254 | 31.75 | 95.8501 | 95.7325 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.43 | #REF! | 25.67 | 20.86 | 46.53 | 47.96 | 11.99 | 98.4365 | 98.3884 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 136 | #REF! | 106.05 | 86 | 192.05 | 328.05 | 10.935 | 99.1396 | 98.5302 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 98.1 | #REF! | 65.17 | 45.38 | 110.55 | 208.65 | 13.91 | 99.0094 | 98.1304 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 53.24 | #REF! | 62.3 | 46.29 | 108.59 | 161.83 | 13.4858 | 98.7837 | 98.1874 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 0 | #REF! | 1641.7 | 2777.5 | 4419.2 | 4419.2 | 90.1878 | 87.878 | 87.878 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 133.8 | #REF! | 2744.7 | 3320.1 | 6064.8 | 6198.6 | 105.061 | 86.1837 | 85.8789 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 55.4 | #REF! | 680.7 | 377 | 1057.7 | 1113.1 | 23.1896 | 97.0383 | 96.8831 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 22.2 | #REF! | 300 | 160.7 | 460.7 | 482.9 | 13.4139 | 98.2799 | 98.1971 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 186.95 | #REF! | 126.15 | 54.38 | 180.53 | 367.48 | 14.1338 | 99.0667 | 98.1003 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 70.01 | #REF! | 70.01 | 27.16 | 97.17 | 167.18 | 1.3164 | 99.8972 | 99.8231 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 22.81 | #REF! | 50.91 | 27.25 | 78.16 | 100.97 | 4.2071 | 99.5623 | 99.4345 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 14.25 | #REF! | 130.43 | 55.84 | 186.27 | 200.52 | 28.6457 | 96.4234 | 96.1498 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 0.39 | #REF! | 6.79 | 1.78 | 8.57 | 8.96 | 0.40727 | 99.9476 | 99.9453 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
516
Note: The Outage due to incoming supply failure for Devanahlli has been confirmed as Zero from concerned circle for the month of Aug-16
|  | 516 | 516 | 866.7047 | #REF! | 6931.07 | 7405.56 | 14336.63 | 15203.3347 | 675.1247 | 96.1411 | 95.9078 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
20000
5000
5000
8000
18000
2000
[11 empty] | 2516.6708 | 2509.2574 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 96.795 | 96.5099 |  |  | #REF! | #REF!

## Aug ANXIII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Aug-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Aug-2016 |  |  |  | Reliability for cummulative period From Apilr-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 229 | 226 | 180.2 | #REF! | 4354 | 2826.52 | 7180.52 | 7360.72 | 32.1429 | 94.3806 | 94.2396 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 167 | 167 | 43 | #REF! | 5850.67 | 2942.9 | 8793.57 | 8836.57 | 52.9136 | 90.5634 | 90.5173 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 125.4 | #REF! | 3339.33 | 3378.57 | 6717.9 | 6843.3 | 38.4455 | 93.2364 | 93.1101 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 190 | 190 | 45.2802 | #REF! | 2763.17 | 1045.36 | 3808.53 | 3853.8102 | 20.2832 | 96.4077 | 96.365 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 365 | 65 | #REF! | 4534 | 6472 | 11006 | 11071 | 28.7558 | 94.8769 | 94.8466 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.0833
6 | Tiptur | 187 | 187 | 84 | #REF! | 3125.35 | 2146.35 | 5271.7 | 5355.7 | 28.6401 | 94.9479 | 94.8674 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.4
7 | Madhugiri | 272 | 272 | 38 | #REF! | 4360 | 2767 | 7127 | 7165 | 26.3419 | 95.3043 | 95.2792 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.63333
8 | Kolar | 134 | 134 | 38.7 | #REF! | 726.23 | 398.1 | 1124.33 | 1163.03 | 8.6793 | 98.4963 | 98.4446 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 161 | 161 | 215 | #REF! | 368 | 136.8 | 504.8 | 719.8 | 4.4708 | 99.4381 | 99.1988 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.5833
10 | CB Pura | 173 | 173 | 194.2 | #REF! | 313.35 | 242.11 | 555.46 | 749.66 | 4.3333 | 99.4246 | 99.2234 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2367
11 | Chintamani | 120 | 120 | 56.3 | #REF! | 572.45 | 407.5 | 979.95 | 1036.25 | 8.6354 | 98.5365 | 98.4524 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 33 | 33 | 35.25 | #REF! | 529.16 | 519.2 | 1048.36 | 1083.61 | 32.8367 | 94.3067 | 94.1153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 89.85 | #REF! | 936.7 | 1287.5 | 2224.2 | 2314.05 | 74.6468 | 87.1419 | 86.6224 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 64 | 64 | 125.1 | #REF! | 1465.86 | 1806.7 | 3272.56 | 3397.66 | 53.0884 | 90.8362 | 90.4859 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 12.07 | #REF! | 80.32 | 122.83 | 203.15 | 215.22 | 15.3729 | 97.3995 | 97.245 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 3.6 | #REF! | 160.5 | 401.5 | 562 | 565.6 | 16.16 | 97.1224 | 97.1039 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 639.98 | #REF! | 519.5 | 395.95 | 915.45 | 1555.43 | 38.8858 | 95.8985 | 93.0312 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 655.65 | #REF! | 760.32 | 920.28 | 1680.6 | 2336.25 | 26.25 | 96.6159 | 95.2957 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.52 | #REF! | 6.6 | 4.8 | 11.4 | 11.92 | 0.62737 | 99.8925 | 99.8876 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 43.27 | #REF! | 81.1 | 38 | 119.1 | 162.37 | 4.7756 | 99.3722 | 99.1442 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 26.17 | #REF! | 363.1 | 243.8 | 606.9 | 633.07 | 13.4696 | 97.6859 | 97.5861 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 69.44 | #REF! | 444.2 | 281.8 | 726 | 795.44 | 9.8202 | 98.3937 | 98.2401 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 6.66 | #REF! | 61.4 | 39.8 | 101.2 | 107.86 | 1.6853 | 99.7166 | 99.698 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 2747 | 2189 | 2578.96 | #REF! | 23762.14 | 21458.54 | 45220.68 | 47799.64 | 429.6182 | 97.1308 | 96.9672 | #REF! | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
0
0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1924.1489 | 1918.9782
|  | 2513 | [8 empty] | 96.2074 | 95.9489
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2513
|  | 1420 | [7 empty] | 6655.66 |  |  |  |  | #REF! | #REF!
529
4462
138.87

## Sheet1 (hidden)
Annexure I | Total Number of feeders | Annexure II | Total Number of feeders | Annexure III | Total Number of feeders
Davangere | 34 | Jagalur | 1 | Davangere | 229
Chitradurga | 11 | Channagiri | 1 | Harihara | 167
Tumkur | 30 | Harihara | 11 | Chitradurga | 178
Bangalore Urban | 1335 | Honnali | 2 | Hiriyur | 190
Ramanagara | 4 | Harapanahalli | 4 | Tumkur | 385
Kolar | 12 | Holalkere | 1 | Tiptur | 187
CBPura | 9 | Hosadurga | 2 | Madhugiri | 272
| 1435 | Hiriyur | 3 | Kolar | 134
|  | Challakere | 5 | KGF | 161
|  | Molakalmuru | 1 | CB Pura | 173
|  | Tumkur | 7 | Chintamani | 120
|  | Tiptur | 11 | Devanahalli | 33
|  | Madhugiri | 8 | Hosakote | 31
|  | Srinivaspura | 4 | Yelahanka | 64
|  | KGF | 30 | Nelamangala | 14
|  | CB Pura | 15 | Doddaballapura | 35
|  | Chintamani | 12 | Magadi | 40
|  | Devanahalli | 49 | Nelamangala | 89
|  | Hosakote | 59 | Chandapura | 19
|  | Nelamangala | 48 | Ramanagara | 34
|  | Doddaballapura | 36 | Channapatna | 47
|  | Magadi | 26 | Ramanagara | 81
|  | Anekal | 127 | Kanakapura | 64
|  | Ramanagara | 24 |  | 2747
|  | Channapatna | 7
|  | Kanakapura | 22 |  |  | 4698
516
Total number of Feeders BESCOM as a whole as per RI Annexure I,II,III=4698

## Sep ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Sep-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Sep-2016 |  |  |  | Reliability for cummulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 27.08 | #REF! | 98.9617 | 98.8511 | 197.8128 | 224.8928 | 6.6145 | 99.1919 | 99.0813 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 5.5 | #REF! | 200.76 | 132.52 | 333.28 | 338.78 | 30.7982 | 95.7919 | 95.7225 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 62 | #REF! | 346 | 144 | 490 | 552 | 18.4 | 97.7315 | 97.4444 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1338 | 1120 | 517.41 | #REF! | 5064.26 | 2953.05 | 8017.31 | 8534.72 | 6.3787 | 99.1678 | 99.1141 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 9.04 | #REF! | 33.79 | 24.27 | 58.06 | 67.1 | 16.775 | 97.984 | 97.6701 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 1.7 | #REF! | 98.23 | 60.03 | 158.26 | 159.96 | 13.33 | 98.1683 | 98.1486 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 18.45 | #REF! | 55.25 | 46.1 | 101.35 | 119.8 | 13.3111 | 98.436 | 98.1512 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1435 | 1214 | 657.93 | #REF! | 5854.2717 | 3444.8911 | 9299.1628 | 9957.0928 | 105.5886 | 99.1 | 98.8608 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
686.1
98.0143

## Sep ANXII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Sep-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Sep-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 4.31 | #REF! | 8.35 | 2.7 | 11.05 | 15.36 | 15.36 | 98.4653 | 97.8667 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 2 | #REF! | 23 | 1.45 | 24.45 | 26.45 | 26.45 | 96.6042 | 96.3264 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 9.3 | #REF! | 84.16 | 30.45 | 114.61 | 123.91 | 11.2645 | 98.5529 | 98.4355 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 7.05 | #REF! | 48.6 | 5.3 | 53.9 | 60.95 | 30.475 | 96.2569 | 95.7674 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 1.4 | #REF! | 21.75 | 2.1 | 23.85 | 25.25 | 6.3125 | 99.1719 | 99.1233 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 4.2 | #REF! | 20.71 | 10.62 | 31.33 | 35.53 | 35.53 | 95.6486 | 95.0653 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 6.5 | #REF! | 45.23 | 33.68 | 78.91 | 85.41 | 42.705 | 94.5201 | 94.0687 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 11.5262 | #REF! | 26.63 | 15.15 | 41.78 | 53.3062 | 17.7687 | 98.0657 | 97.5321 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 13.3648 | #REF! | 20.08 | 21.97 | 42.05 | 55.4148 | 11.083 | 98.8319 | 98.4607 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 1.8285 | #REF! | 5.7 | 2.55 | 8.25 | 10.0785 | 10.0785 | 98.8542 | 98.6002 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 9.5 | #REF! | 172.45 | 70.4 | 242.85 | 252.35 | 36.05 | 95.1815 | 94.9931 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 15.3 | #REF! | 151.85 | 64.6 | 216.45 | 231.75 | 21.0682 | 97.267 | 97.0739 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 8.5 | #REF! | 160 | 87 | 247 | 255.5 | 31.9375 | 95.7118 | 95.5642 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.43 | #REF! | 30.26 | 25.43 | 55.69 | 57.12 | 14.28 | 98.0663 | 98.0167 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 144 | #REF! | 109 | 94 | 203 | 347 | 11.5667 | 99.0602 | 98.3935 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 83.05 | #REF! | 64.25 | 48.2 | 112.45 | 195.5 | 13.0333 | 98.9588 | 98.1898 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 34.76 | #REF! | 59.38 | 54.22 | 113.6 | 148.36 | 12.3633 | 98.6852 | 98.2829 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 174.4 | #REF! | 1521.9 | 2359.9 | 3881.8 | 4056.2 | 82.7796 | 88.9972 | 88.5028 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 259.8 | #REF! | 2115.7 | 2719.9 | 4835.6 | 5095.4 | 86.3627 | 88.6168 | 88.0052 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 0.7 | #REF! | 504.5 | 269 | 773.5 | 774.2 | 16.1292 | 97.7619 | 97.7598 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 73.7 | #REF! | 330.8 | 563.9 | 894.7 | 968.4 | 26.9 | 96.5482 | 96.2639 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 46.29 | #REF! | 131.14 | 31.22 | 162.36 | 208.65 | 8.025 | 99.1327 | 98.8854 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 51.27 | #REF! | 51.2701 | 21.8111 | 73.0812 | 124.3512 | 0.97914 | 99.9201 | 99.864 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 5.25 | #REF! | 37.27 | 18.76 | 56.03 | 61.28 | 2.5533 | 99.6758 | 99.6454 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 69.78 | #REF! | 159.34 | 17.85 | 177.19 | 246.97 | 35.2814 | 96.4843 | 95.0998 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 0.32639 | #REF! | 5.725 | 1.9181 | 7.6431 | 7.9694 | 0.36225 | 99.9517 | 99.9497 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
516
Note: The Outage due to incoming supply failure for Devanahlli has been confirmed as Zero from concerned circle for the month of Aug-16
|  | 516 | 516 | 1039.5358 | #REF! | 5909.0451 | 6574.0792 | 12483.1243 | 13522.6601 | 606.6988 | 96.64 | 96.3602 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
20000
5000
5000
8000
18000
2000
[11 empty] | 2524.9913 | 2515.7363 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 97.115 | 96.7591 |  |  | #REF! | #REF!

## Sep ANXIII (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Sep-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Sep-2016 |  |  |  | Reliability for cummulative period From Apilr-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 229 | 226 | 42.15 | #REF! | 4145.925 | 3016.33 | 7162.255 | 7204.405 | 31.4603 | 94.2081 | 94.174 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 167 | 167 | 82.61 | #REF! | 4656.08 | 2702.88 | 7358.96 | 7441.57 | 44.5603 | 91.8397 | 91.7481 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 132.5 | #REF! | 3329.99 | 3328.51 | 6658.5 | 6791 | 38.1517 | 93.0727 | 92.9349 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 190 | 190 | 46.1858 | #REF! | 1938 | 980.94 | 2918.94 | 2965.1258 | 15.6059 | 97.155 | 97.11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 365 | 65 | #REF! | 3241 | 5056 | 8297 | 8362 | 21.7195 | 96.0091 | 95.9779 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.0833
6 | Tiptur | 187 | 187 | 84 | #REF! | 2037 | 1969 | 4006 | 4090 | 21.8717 | 96.0329 | 95.9497 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.4
7 | Madhugiri | 272 | 272 | 38 | #REF! | 4327 | 2773 | 7100 | 7138 | 26.2426 | 95.1661 | 95.1403 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.63333
8 | Kolar | 134 | 134 | 178.7 | #REF! | 442 | 323.23 | 765.23 | 943.93 | 7.0443 | 98.9425 | 98.6955 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 161 | 161 | 206 | #REF! | 362 | 178 | 540 | 746 | 4.6335 | 99.3789 | 99.1419 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.4333
10 | CB Pura | 173 | 173 | 235.25 | #REF! | 269.15 | 249.54 | 518.69 | 753.94 | 4.358 | 99.4448 | 99.193 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.9208
11 | Chintamani | 120 | 120 | 168.033 | #REF! | 550.53 | 437.25 | 987.78 | 1155.813 | 9.6318 | 98.4756 | 98.2163 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 185.18 | #REF! | 373.45 | 491.27 | 864.72 | 1049.9 | 30.8794 | 95.2902 | 94.2816 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 287.33 | #REF! | 556.3 | 883.92 | 1440.22 | 1727.55 | 55.7274 | 91.3965 | 89.6801 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 472.51 | #REF! | 929.75 | 1375.19 | 2304.94 | 2777.45 | 42.73 | 93.4332 | 92.087 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 0 | #REF! | 81.56 | 94.53 | 176.09 | 176.09 | 12.5779 | 97.6708 | 97.6708 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 96.6 | #REF! | 151.25 | 467.1 | 618.35 | 714.95 | 20.4271 | 96.7283 | 96.2172 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 48.05 | #REF! | 526.05 | 280.25 | 806.3 | 854.35 | 21.3587 | 96.2671 | 96.0447 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 144.65 | #REF! | 758.86 | 841.88 | 1600.74 | 1745.39 | 19.6111 | 96.6693 | 96.3683 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.47 | #REF! | 6.3 | 4.5 | 10.8 | 11.27 | 0.59316 | 99.8947 | 99.8902 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 26.75 | #REF! | 41 | 25.7 | 66.7 | 93.45 | 2.7485 | 99.6367 | 99.491 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 78.8 | #REF! | 274.7 | 142.2 | 142.2364 | 221.0364 | 4.7029 | 99.4396 | 99.1291 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 105.55 | #REF! | 315.7 | 167.9 | 483.6 | 589.15 | 7.2735 | 98.8944 | 98.6531 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 6.66 | #REF! | 44.9 | 30 | 74.9 | 81.56 | 1.2744 | 99.7833 | 99.764 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 2749 | 2191 | 2469.683 | #REF! | 19434.425 | 18806.79 | 37966.5514 | 40436.2344 | 346.8658 | 97.5933 | 97.4367 | #REF! | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
0
0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1935.8327 | 1930.4502
|  | 2514 | [8 empty] | 96.7916 | 96.5225
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2514
|  | 1420 | [7 empty] | 6035.45 |  |  |  |  | #REF! | #REF!
529
4463
138.87

## Oct ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Oct-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Oct-2016 |  |  |  | Reliability for cummulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 27.08 | #REF! | 195.96 | 58.21 | 254.17 | 281.25 | 8.2721 | 98.9952 | 98.8882 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 12.6 | #REF! | 216.99 | 150.39 | 367.38 | 379.98 | 34.5436 | 95.511 | 95.357 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 82 | #REF! | 334 | 113 | 447 | 529 | 17.6333 | 97.9973 | 97.6299 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1342 | 1123 | 660.42 | #REF! | 3820 | 3292.11 | 7112.11 | 7772.53 | 5.7918 | 99.2877 | 99.2215 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 8.52 | #REF! | 30.18 | 19.58 | 49.76 | 58.28 | 14.57 | 98.328 | 98.0417 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 1.4 | #REF! | 78.03 | 51.03 | 129.06 | 130.46 | 10.8717 | 98.5544 | 98.5388 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 63 | #REF! | 45.31 | 30.21 | 75.52 | 138.52 | 15.3911 | 98.8722 | 97.9313 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1439 | 1217 | 916.62 | #REF! | 4687.75 | 3693.71 | 8381.46 | 9298.08 | 111.593 | 99.2171 | 99.1315 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
[6 empty] | 3820:00 | 3292:11
686.1
98.0143

## oct ANX II (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Oct-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Oct-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 4.31 | #REF! | 8.35 | 2.7 | 11.05 | 15.36 | 15.36 | 98.5148 | 97.9355 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 2 | #REF! | 23 | 1.45 | 24.45 | 26.45 | 26.45 | 96.7137 | 96.4449 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 1.4 | #REF! | 27.125 | 9.07 | 36.195 | 37.595 | 3.4177 | 99.5577 | 99.5406 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 2 | #REF! | 28 | 4.6 | 32.6 | 34.6 | 17.3 | 97.8091 | 97.6747 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 1.35 | #REF! | 23.5 | 3.15 | 26.65 | 28 | 7 | 99.1045 | 99.0591 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 6.8 | #REF! | 22.19 | 12.15 | 34.34 | 41.14 | 41.14 | 95.3844 | 94.4704 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 12.6 | #REF! | 48.18 | 36.93 | 85.11 | 97.71 | 48.855 | 94.2802 | 93.4335 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 11.8144 | #REF! | 21.33 | 27.03 | 48.36 | 60.1744 | 20.0581 | 97.8333 | 97.304 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 13.6989 | #REF! | 16.42 | 11.08 | 27.5 | 41.1989 | 8.2398 | 99.2608 | 98.8925 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 1.8742 | #REF! | 6.05 | 1.4 | 7.45 | 9.3242 | 9.3242 | 98.9987 | 98.7468 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 15 | #REF! | 189 | 103 | 292 | 307 | 43.8571 | 94.3932 | 94.1052 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 20 | #REF! | 133 | 186 | 319 | 339 | 30.8182 | 96.1022 | 95.8578 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 8 | #REF! | 134 | 85 | 219 | 227 | 28.375 | 96.3206 | 96.1862 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.24 | #REF! | 30.43 | 25.34 | 55.77 | 57.01 | 14.2525 | 98.126 | 98.0843 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 167 | #REF! | 106 | 96 | 202 | 369 | 12.3 | 99.095 | 98.3468 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 97.35 | #REF! | 52.4 | 40.05 | 92.45 | 189.8 | 12.6533 | 99.1716 | 98.2993 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 55.9192 | #REF! | 58.3 | 38.48 | 96.78 | 152.6992 | 12.7249 | 98.916 | 98.2897 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 182.25 | #REF! | 1521.85 | 2359.85 | 3881.7 | 4063.95 | 82.9378 | 89.3524 | 88.8525 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 278.37 | #REF! | 2407.22 | 2973.65 | 5380.87 | 5659.24 | 95.9193 | 87.7418 | 87.1076 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 12.4 | #REF! | 572.08 | 557.65 | 1129.73 | 1142.13 | 23.7944 | 96.8366 | 96.8018 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 25.7 | #REF! | 241.1 | 103.55 | 344.65 | 370.35 | 10.2875 | 98.7132 | 98.6173 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 62.24 | #REF! | 400.39 | 351.04 | 751.43 | 813.67 | 31.295 | 96.1154 | 95.7937 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 53.2542 | #REF! | 53.2542 | 20.2569 | 73.5111 | 126.7653 | 0.99815 | 99.9222 | 99.8658 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 8.53 | #REF! | 28.37 | 40.38 | 68.75 | 77.28 | 3.22 | 99.615 | 99.5672 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 4.81 | #REF! | 146.64 | 35.11 | 181.75 | 186.56 | 26.6514 | 96.5102 | 96.4178 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 0.32639 | #REF! | 7.4132 | 2.5417 | 9.9549 | 10.2813 | 0.46733 | 99.9392 | 99.9372 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
516
Note: The Outage due to incoming supply failure for Devanahlli has been confirmed as Zero from concerned circle for the month of Aug-16
|  | 516 | 516 | 1050.2372 | #REF! | 6305.5924 | 7127.4586 | 13433.051 | 14483.2881 | 627.6968 | 96.3843 | 96.1016 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
20000
5000
5000
8000
18000
2000
[11 empty] | 2524.3277 | 2515.6322 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 97.0895 | 96.7551 |  |  | #REF! | #REF!

## oct ANX III (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Oct-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Oct-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 229 | 226 | 42.15 | #REF! | 4145.925 | 3016.33 | 7162.255 | 7204.405 | 31.4603 | 94.3949 | 94.362 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 167 | 167 | 23.8 | #REF! | 2211.57 | 1470.86 | 3682.43 | 3706.23 | 22.193 | 96.0483 | 96.0228 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 188.52 | #REF! | 3592.54 | 3617.58 | 7210.12 | 7398.64 | 41.5654 | 92.7408 | 92.551 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 192 | 192 | 47.1095 | #REF! | 1895.73 | 1034.5 | 2930.23 | 2977.3395 | 15.507 | 97.2649 | 97.221 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 385 | 57 | #REF! | 5026 | 6600 | 11626 | 11683 | 30.3455 | 94.5883 | 94.5617 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.95
6 | Tiptur | 187 | 187 | 49 | #REF! | 2091 | 2209 | 4300 | 4349 | 23.2567 | 95.8791 | 95.8321 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.81667
7 | Madhugiri | 272 | 272 | 45 | #REF! | 3627 | 2316 | 5943 | 5988 | 22.0147 | 96.0844 | 96.0547 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.75
8 | Kolar | 134 | 134 | 40.26 | #REF! | 543.02 | 426.32 | 969.34 | 1009.6 | 7.5343 | 98.7036 | 98.6498 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 170 | 170 | 236 | #REF! | 458 | 141 | 599 | 835 | 4.9118 | 99.3685 | 99.1198 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.9333
10 | CB Pura | 173 | 173 | 453.3 | #REF! | 235.03 | 173.21 | 408.24 | 861.54 | 4.98 | 99.5771 | 99.1075 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7.555
11 | Chintamani | 120 | 120 | 56.356 | #REF! | 402.29 | 280.58 | 682.87 | 739.226 | 6.1602 | 98.9802 | 98.896 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 208.17 | #REF! | 404.4167 | 652.3833 | 1056.8 | 1264.97 | 37.205 | 94.4297 | 93.3324 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 321.74 | #REF! | 530.6167 | 1113.0333 | 1643.65 | 1965.39 | 63.3997 | 90.498 | 88.6381 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 529.91 | #REF! | 935.0333 | 1765.4167 | 2700.45 | 3230.36 | 49.6978 | 92.5546 | 91.0936 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 11.68 | #REF! | 88.39 | 145.32 | 233.71 | 245.39 | 17.5279 | 97.0083 | 96.8588 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 53.45 | #REF! | 4285.4 | 554.79 | 4840.19 | 4893.64 | 139.8183 | 75.2166 | 74.943 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 339.75 | #REF! | 319.55 | 751.4 | 1070.95 | 1410.7 | 35.2675 | 95.2018 | 93.6797 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 404.88 | #REF! | 4693.34 | 1451.51 | 6144.85 | 6549.73 | 73.5925 | 87.6267 | 86.8114 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.43 | #REF! | 8.2167 | 4.4854 | 12.7021 | 13.1321 | 0.69116 | 99.8802 | 99.8761 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 26.99 | #REF! | 112.67 | 22.21 | 134.88 | 161.87 | 4.7609 | 99.2891 | 99.1468 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 11.76 | #REF! | 177.179 | 68.2536 | 142.2364 | 153.9964 | 3.2765 | 99.4577 | 99.4128 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 38.75 | #REF! | 289.849 | 90.4636 | 380.3126 | 419.0626 | 5.1736 | 99.1586 | 99.0728 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 52.0879 | #REF! | 119.3 | 38.8187 | 158.1187 | 210.2067 | 3.2845 | 99.5572 | 99.4114 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 2760 | 2220 | 2978.6639 |  |  | 21820.5247 | 50209.5549 | 53188.2188 | 564.3587 | 96.7398 | 96.5464 | #REF! | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
0
0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1914.1688 | 1907.6774
|  | 2525 | [8 empty] | 95.7084 | 95.3839
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2525
|  | 1420 | [7 empty] | 6488.36 |  |  |  |  | #REF! | #REF!
529
4474
138.87

## Nov ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Nov-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Nov-2016 |  |  |  | Reliability for cummulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=14/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 3.1 | #REF! | 179.65 | 26.85 | 206.5 | 209.6 | 6.1647 | 99.1565 | 99.1438 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 10.5 | #REF! | 214.29 | 153.08 | 367.37 | 377.87 | 34.3518 | 95.5111 | 95.3828 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 70 | #REF! | 347 | 162 | 509 | 579 | 19.3 | 97.7195 | 97.4059 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1342 | 1136 | 728 | #REF! | 3546 | 2768 | 6314 | 7042 | 5.2474 | 99.3676 | 99.2947 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 8.8 | #REF! | 6.3271 | 7.1958 | 13.5229 | 22.3229 | 5.5807 | 99.5456 | 99.2499 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 12 | 12 | 1.06 | #REF! | 86.11 | 55.92 | 142.03 | 143.09 | 11.9242 | 98.4092 | 98.3973 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 22.05 | #REF! | 41 | 35.36 | 76.36 | 98.41 | 10.9344 | 98.8596 | 98.5303 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1439 | 1230 | 864.5 | #REF! | 4375.2671 | 3187.8458 | 7563.1129 | 8427.6129 | 92.5135 | 99.2936 | 99.2128 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
[6 empty] | 3820:00 | 3292:11
686.1
98.0143

## Nov ANX II (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Nov-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Nov-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 22.2 | #REF! | 5.85 | 1.5 | 7.35 | 29.55 | 29.55 | 98.9792 | 95.8958 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 12.1 | #REF! | 22.5 | 0.35 | 22.85 | 34.95 | 34.95 | 96.8264 | 95.1458 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 5.89 | #REF! | 49.34 | 30.33 | 79.67 | 85.56 | 7.7782 | 98.9941 | 98.9197 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 3.5 | #REF! | 36.5 | 3.1 | 39.6 | 43.1 | 21.55 | 97.25 | 97.0069 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 3.4 | #REF! | 25.8 | 0.85 | 26.65 | 30.05 | 7.5125 | 99.0747 | 98.9566 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 5.6 | #REF! | 21.94 | 12.49 | 34.43 | 40.03 | 40.03 | 95.2181 | 94.4403 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 11.5 | #REF! | 47.69 | 37.42 | 85.11 | 96.61 | 48.305 | 94.0896 | 93.291 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 12.1097 | #REF! | 61.9 | 4.35 | 66.25 | 78.3597 | 26.1199 | 96.9329 | 96.3722 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 14.0414 | #REF! | 13.6 | 7.2 | 20.8 | 34.8414 | 6.9683 | 99.4222 | 99.0322 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 1.921 | #REF! | 9.8 | 1.45 | 11.25 | 13.171 | 13.171 | 98.4375 | 98.1707 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 10 | #REF! | 100 | 250 | 350 | 360 | 51.4286 | 93.0556 | 92.8571 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 13 | #REF! | 167 | 283 | 450 | 463 | 42.0909 | 94.3182 | 94.154 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 10 | #REF! | 80 | 204 | 284 | 294 | 36.75 | 95.0694 | 94.8958 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.2 | #REF! | 45.8 | 36.8 | 82.6 | 83.8 | 20.95 | 97.1319 | 97.0903 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 150 | #REF! | 159 | 90 | 249 | 399 | 13.3 | 98.8472 | 98.1528 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 75.25 | #REF! | 76.27 | 58.05 | 134.32 | 209.57 | 13.9713 | 98.7563 | 98.0595 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 44.1 | #REF! | 56.64 | 39.12 | 95.76 | 139.86 | 11.655 | 98.8917 | 98.3812 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 154.7 | #REF! | 1476.3167 | 2572.0667 | 4048.3833 | 4203.0833 | 85.7772 | 88.525 | 88.0865 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 250.82 | #REF! | 2361.6867 | 3185.8667 | 5547.5533 | 5798.3733 | 98.2775 | 86.9408 | 86.3503 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 189.2 | #REF! | 543.15 | 288.69 | 831.84 | 1021.04 | 21.2717 | 97.5931 | 97.0456 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 6.4 | #REF! | 654.9 | 1184.1 | 1839 | 1845.4 | 51.2611 | 92.9051 | 92.8804 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 59.7 | #REF! | 149 | 34.94 | 183.94 | 243.64 | 9.3708 | 99.0174 | 98.6985 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 49.5938 | #REF! | 49.5938 | 22.9049 | 72.4986 | 122.0924 | 0.96136 | 99.9207 | 99.8665 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 6.48 | #REF! | 21.3147 | 35.0764 | 56.3911 | 62.8711 | 2.6196 | 99.6737 | 99.6362 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 28.58 | #REF! | 49.3687 | 15.3632 | 64.7319 | 93.3119 | 13.3303 | 98.7156 | 98.1486 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 3.9064 | #REF! | 4.8215 | 1.2431 | 6.0646 | 9.971 | 0.45323 | 99.9617 | 99.9371 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
516
Note: The Outage due to incoming supply failure for Devanahlli has been confirmed as Zero from concerned circle for the month of Aug-16
|  | 516 | 516 | 1145.1923 | #REF! | 6289.7821 | 8400.2608 | 14690.0429 | 15835.2352 | 709.4035 | 96.046 | 95.7377 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
98.4167
20000
5000
5000
8000
18000
2000
[11 empty] | 2514.5479 | 2501.4717 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 96.7134 | 96.2105 |  |  | #REF! | #REF!

## Nov ANX III (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Nov-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Nov-2016 |  |  |  | Reliability for cummulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 229 | 226 | 302.46 | #REF! | 3872.31 | 1083.68 | 4955.99 | 5258.45 | 22.9627 | 95.9922 | 95.7477 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 172 | 172 | 54.69 | #REF! | 2642.812 | 724.02 | 3366.832 | 3421.522 | 19.8926 | 96.3751 | 96.3162 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 175.26 | #REF! | 3548.93 | 3661.19 | 7210.12 | 7385.38 | 41.4909 | 92.4988 | 92.3165 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 192 | 192 | 48.0517 | #REF! | 1383.24 | 553.99 | 1937.23 | 1985.2817 | 10.34 | 98.1315 | 98.0852 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 365 | 40.2 | #REF! | 4856 | 3458 | 8314 | 8354.2 | 21.6992 | 96.001 | 95.9816 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.67
6 | Tiptur | 187 | 187 | 50.15 | #REF! | 3049 | 2499 | 5548 | 5598.15 | 29.9366 | 94.5058 | 94.4562 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.83583
7 | Madhugiri | 272 | 272 | 45.35 | #REF! | 2871 | 1372 | 4243 | 4288.35 | 15.766 | 97.1112 | 97.0804 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.75583
8 | Kolar | 134 | 134 | 41.28 | #REF! | 430.45 | 303.69 | 734.14 | 775.42 | 5.7867 | 98.9854 | 98.9284 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 170 | 170 | 205 | #REF! | 484 | 148 | 632 | 837 | 4.9235 | 99.3115 | 99.0882 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.4167
10 | CB Pura | 173 | 173 | 287.5 | #REF! | 220.05 | 201.19 | 421.24 | 708.74 | 4.0968 | 99.5491 | 99.2413 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.7917
11 | Chintamani | 120 | 120 | 39.53 | #REF! | 360 | 211.25 | 571.25 | 610.78 | 5.0898 | 99.1184 | 99.0574 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 105.77 | #REF! | 458.8667 | 340.2 | 799.0667 | 904.8367 | 26.6128 | 95.6478 | 95.0717 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 191.59 | #REF! | 614.3267 | 477.13 | 1091.4567 | 1283.0467 | 41.3886 | 93.4799 | 92.3354 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 297.36 | #REF! | 1073.1933 | 817.33 | 1890.5233 | 2187.8833 | 33.6597 | 94.6139 | 93.7667 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 10.32 | #REF! | 70.59 | 120.74 | 191.33 | 201.65 | 14.4036 | 97.4692 | 97.3327 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 19.2 | #REF! | 140.3 | 299.75 | 440.05 | 459.25 | 13.1214 | 97.6717 | 97.5701 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 269.25 | #REF! | 226.65 | 158.65 | 385.3 | 654.55 | 16.3637 | 98.2162 | 96.9697 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 298.77 | #REF! | 437.54 | 579.14 | 1016.68 | 1315.45 | 14.7803 | 97.8846 | 97.2629 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.43 | #REF! | 7.609 | 4.4854 | 12.0944 | 12.5244 | 0.65918 | 99.8821 | 99.8779 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 22.69 | #REF! | 19.6156 | 13.6961 | 33.3117 | 56.0017 | 1.6471 | 99.8186 | 99.695 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 128.83 | #REF! | 177.179 | 68.2536 | 142.2364 | 271.0664 | 5.7674 | 99.4396 | 98.932 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 151.52 | #REF! | 196.7946 | 81.9497 | 278.7443 | 430.2643 | 5.3119 | 99.3627 | 99.0163 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 10.0879 | #REF! | 129.7201 | 17.8035 | 147.5236 | 157.6115 | 2.4627 | 99.5731 | 99.5439 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 2765 | 2200 | 2517.2879 |  |  | 12255.9383 | 31847.9371 | 34365.225 | 286.4399 |  |  |  | #REF! |  |  | 0
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
[7 empty] | 3.42 | [9 empty] | 0
[7 empty] | 0.47 | [9 empty] | 0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1948.7785 | 1943.6275
|  | 2530 | [8 empty] | 97.4389 | 97.1814
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2530
|  | 1420 | [7 empty] | 5445.8833 |  |  |  |  | #REF! | #REF!
529
4479
138.87

## DEC ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Dec-16 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Dec-2016 |  |  |  | Reliability for cumulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 6.25 | #REF! | 193.59 | 68.6 | 262.19 | 268.44 | 7.8953 | 98.9635 | 98.9388 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 8.4 | #REF! | 206.77 | 152.1 | 358.87 | 367.27 | 33.3882 | 95.615 | 95.5123 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 42 | #REF! | 325 | 148 | 473 | 515 | 17.1667 | 97.8808 | 97.6927 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1342 | 1126 | 732 | #REF! | 4252 | 5127 | 9379 | 10111 | 7.5343 | 99.0606 | 98.9873 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 8.46 | #REF! | 7.5028 | 8.9333 | 16.4361 | 24.8961 | 6.224 | 99.4477 | 99.1634 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 13 | 13 | 1.54 | #REF! | 71.57 | 53.15 | 124.72 | 126.26 | 9.7123 | 98.7105 | 98.6946 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 11.05 | #REF! | 36.41 | 31.05 | 67.46 | 78.51 | 8.7233 | 98.9925 | 98.8275 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1439 | 1220 | 819.21 | #REF! | 5057.6828 | 5566.7333 | 10624.4161 | 11443.6261 | 89.6551 | 99.0076 | 98.9311 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
Note: In kolar head quarters: One new feeder is added at SNR Hosiptal, Kolar town
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation

## DEC ANX II (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Dec-2016 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Dec-2016 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 8.45 | #REF! | 1.7 | 6.25 | 7.95 | 16.4 | 16.4 | 98.9315 | 97.7957 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 0.3 | #REF! | 13.1 | 0.65 | 13.75 | 14.05 | 14.05 | 98.1519 | 98.1116 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 0.6 | #REF! | 67.51 | 31.58 | 99.09 | 99.69 | 9.0627 | 98.7892 | 98.7819 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 0.55 | #REF! | 45.1 | 5.6 | 50.7 | 51.25 | 25.625 | 96.5927 | 96.5558 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 0.32 | #REF! | 38.05 | 1.9 | 39.95 | 40.27 | 10.0675 | 98.6576 | 98.6468 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 4.2 | #REF! | 21.26 | 12.4 | 33.66 | 37.86 | 37.86 | 95.4758 | 94.9113 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 6.8 | #REF! | 46.32 | 37.24 | 83.56 | 90.36 | 45.18 | 94.3844 | 93.9274 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 12.4125 | #REF! | 54.9 | 24.15 | 79.05 | 91.4625 | 30.4875 | 96.4583 | 95.9022 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 14.3924 | #REF! | 28.67 | 47.6 | 76.27 | 90.6624 | 18.1325 | 97.9497 | 97.5628 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 1.9691 | #REF! | 6.25 | 2.05 | 8.3 | 10.2691 | 10.2691 | 98.8844 | 98.6197 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 18.55 | #REF! | 183.15 | 136.45 | 319.6 | 338.15 | 48.3071 | 93.8633 | 93.5071 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 14.95 | #REF! | 122 | 172 | 294 | 308.95 | 28.0864 | 96.4076 | 96.225 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 32.23 | #REF! | 135.67 | 38.92 | 174.59 | 206.82 | 25.8525 | 97.0667 | 96.5252 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1 | #REF! | 21 | 12.63 | 33.63 | 34.63 | 8.6575 | 98.87 | 98.8364 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 148 | #REF! | 134 | 61 | 195 | 343 | 11.4333 | 99.1263 | 98.4633 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 90.55 | #REF! | 59.14 | 38.25 | 97.39 | 187.94 | 12.5293 | 99.1273 | 98.3159 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 54.48 | #REF! | 58.06 | 47.25 | 105.31 | 159.79 | 13.3158 | 98.8205 | 98.2102 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 266.25 | #REF! | 1586.78 | 2934.32 | 4521.1 | 4787.35 | 97.701 | 87.5985 | 86.8681 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 671.85 | #REF! | 2363.7367 | 3122.0367 | 5485.7733 | 6157.6233 | 104.3665 | 87.5028 | 85.9722 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 58.25 | #REF! | 842.72 | 521.03 | 1363.75 | 1422 | 29.625 | 96.1813 | 96.0181 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 72.65 | #REF! | 227 | 256.05 | 483.05 | 555.7 | 15.4361 | 98.1965 | 97.9253 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 36.37 | #REF! | 133.09 | 137.05 | 270.14 | 306.51 | 11.7888 | 98.6035 | 98.4155 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 41.7083 | #REF! | 41.7083 | 29.7514 | 71.4597 | 113.1681 | 0.89109 | 99.9244 | 99.8802 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 14.18 | #REF! | 29.9557 | 29.9029 | 59.8586 | 74.0386 | 3.0849 | 99.6648 | 99.5854 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 41.13 | #REF! | 38.3153 | 15.2278 | 53.5431 | 94.6731 | 13.5247 | 98.9719 | 98.1822 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 5.03 | #REF! | 6.9472 | 2.6479 | 9.5951 | 14.6251 | 0.66478 | 99.9414 | 99.9106 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
Note: The Outage due to incoming supply failure for Devanahlli has been confirmed as Zero from concerned circle for the month of Aug-16
|  | 516 | 516 | 1617.1723 | #REF! | 6306.1332 | 7723.9367 | 14030.0699 | 15647.2421 | 642.3993 | 96.2236 | 95.7883 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
#NAME?
52.4382
98.4167
|  | 2 | 2 | 8
|  | 5 | 5 | 12
|  | 7 | 7 | 18
|  | 2 | 2 | 22
|  | 2 | 2 | 25
|  | 2 | 2 | 42
|  | 4 | 4 | 105 |  |  |  | 20000
|  | 1 | 1 | 54 |  |  |  | 5000
|  | 1 | 1 | 91 |  |  |  | 5000
8000
18000
2000
[11 empty] | 2524.1422 | 2513.656 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 97.0824 | 96.6791 |  |  | #REF! | #REF!

## DEC ANX III (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Dec-2016 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Dec-2016 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 230 | 227 | 112.35 | 1408.56 | 4547.76 | 1765.23 | 6312.99 | 6425.34 | 27.9363 | 95.081 | 94.9935 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 172 | 172 | 71.05 | 749.92 | 3674.34 | 1556.92 | 5231.26 | 5302.31 | 30.8274 | 94.5494 | 94.4754 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 112.5 | 1307.31 | 3427.18 | 3645.35 | 7072.53 | 7185.03 | 40.3653 | 92.8793 | 92.7661 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 192 | 192 | 49.0127 | 408.0546 | 1838.684 | 1429.53 | 3268.214 | 3317.2267 | 17.2772 | 96.9495 | 96.9037 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 365 | 38 | 806.6 | 4873.85 | 9405.55 | 14279.4 | 14317.4 | 37.1881 | 93.3532 | 93.3355 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.63333
6 | Tiptur | 187 | 187 | 52 | 807.45 | 2583 | 5013 | 7596 | 7648 | 40.8984 | 92.7204 | 92.6705 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.86667
7 | Madhugiri | 289 | 289 | 47 | 676.41 | 4185.333 | 4729.083 | 8914.416 | 8961.416 | 31.0084 | 94.4721 | 94.4429 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.78333
8 | Kolar | 134 | 134 | 50.6 | #REF! | 231.04 | 225.6 | 456.64 | 507.24 | 3.7854 | 99.3893 | 99.3216 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 170 | 170 | 269 | #REF! | 524 | 161 | 685 | 954 | 5.6118 | 99.2779 | 98.9943 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.4833
10 | CB Pura | 173 | 173 | 477.5 | #REF! | 212.1 | 193.03 | 405.13 | 882.63 | 5.1019 | 99.5803 | 99.0857 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7.9583
11 | Chintamani | 120 | 120 | 33.2 | #REF! | 424.1 | 324.4 | 748.5 | 781.7 | 6.5142 | 98.8822 | 98.8326 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 118.74 | #REF! | 462.6667 | 849.3167 | 1311.9833 | 1430.7233 | 42.0801 | 93.0846 | 92.4588 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 234.97 | #REF! | 621.9867 | 1204.6167 | 1826.6033 | 2061.5733 | 66.5024 | 89.4404 | 88.082 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 353.71 | #REF! | 1084.6533 | 2053.9333 | 3138.5867 | 3492.2967 | 53.7276 | 91.3466 | 90.3714 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 6.77 | #REF! | 78.01 | 246.97 | 324.98 | 331.75 | 23.6964 | 95.84 | 95.7533 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 32.4 | #REF! | 226.7 | 640 | 866.7 | 899.1 | 25.6886 | 95.5622 | 95.3963 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 48 | #REF! | 473.85 | 208.25 | 682.1 | 730.1 | 18.2525 | 96.944 | 96.7289 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 87.17 | #REF! | 778.56 | 1095.22 | 1873.78 | 1960.95 | 22.0331 | 96.2269 | 96.0514 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.39 | #REF! | 7.7097 | 6.43 | 14.1397 | 14.5297 | 0.76472 | 99.8666 | 99.863 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 31.83 | #REF! | 61.3458 | 74.6211 | 135.9669 | 167.7969 | 4.9352 | 99.2833 | 99.1156 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 103.6 | #REF! | 80.3315 | 72.3019 | 142.2364 | 245.8364 | 5.2306 | 99.4577 | 99.0626 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 135.43 | #REF! | 141.6773 | 146.9231 | 288.6004 | 424.0304 | 5.2349 | 99.3615 | 99.0618 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 6.5879 | #REF! | 41.4394 | 79.7989 | 121.2383 | 127.8262 | 1.9973 | 99.6605 | 99.6421 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note : * Total No of 11KV Feeders pertaining to Madhugiri Division under Annexure-3 is 289 including Newly comissioned NJY feeders under Phase-3 (earlier 272 feeders). * Total No of 11KV Feeders pertaining to Davanagere Division under Annexure-3 is 230 including Newly comissioned NJY feeder under Phase-3 (earlier 229 feeders).
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
0
0
[15 empty] | 98.57 | 97.92 | -98.57
[7 empty] | 3.42 | [9 empty] | 0
[7 empty] | 0.47 | [9 empty] | 0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1926.2739 | 1921.9244
|  | 2548 | [8 empty] | 96.3137 | 96.0962
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2548
|  | 1420 | [7 empty] | 6750.2967 |  |  |  |  | #REF! | #REF!
529
4497
138.87

## Jan ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Jan'17 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Jan-2017 |  |  |  | Reliability for cumulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 24.35 | #REF! | 210.62 | 52.35 | 262.97 | 287.32 | 8.4506 | 98.9604 | 98.8642 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 12.6 | #REF! | 202.9 | 155.34 | 358.24 | 370.84 | 33.7127 | 95.6227 | 95.4687 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 25 | #REF! | 363 | 71 | 434 | 459 | 15.3 | 98.0556 | 97.9435 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1346 | 1111 | 542 | #REF! | 2960 | 3586 | 6546 | 7088 | 5.266 | 99.3463 | 99.2922 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 1 | #REF! | 27.7632 | 7.2243 | 34.9875 | 35.9875 | 8.9969 | 98.8243 | 98.7907 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 13 | 13 | 1.6 | #REF! | 98.84 | 80.23 | 179.07 | 180.67 | 13.8977 | 98.1486 | 98.132 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 29.2 | #REF! | 51.37 | 43.04 | 94.41 | 123.61 | 13.7344 | 98.5901 | 98.154 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1443 | 636 | #REF! | #REF! | 3867.0232 | 3957.9943 | 7825.0175 | 8488.3675 | 99.1951 | 99.2711 | 99.2093 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
| Note: | Details of new 4 feeders added:
1. South: Gollahalli MUSS, F12 feeder
2. East: HBR MUSS, F18-Nagenahalli feeder
3. North: Hebbal MUSS, F17 P&T Colony feeder.
4. North: Sahakarnagar MUSS, F18 Adhar feeder.
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
113.52

## Jan ANX II (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
B. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Jan-2017 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Jan-2017 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 1.2 | #REF! | 10.65 | 1.25 | 11.9 | 13.1 | 13.1 | 98.4005 | 98.2392 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 2.35 | #REF! | 9.3 | 0.3 | 9.6 | 11.95 | 11.95 | 98.7097 | 98.3938 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 1.86 | #REF! | 274 | 317 | 591 | 592.86 | 53.8964 | 92.7786 | 92.7559 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 7.35 | #REF! | 49.55 | 2.8 | 52.35 | 59.7 | 29.85 | 96.4819 | 95.9879 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 0.25 | #REF! | 1.5 | 0.75 | 2.25 | 2.5 | 0.625 | 99.9244 | 99.916 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 4.8 | #REF! | 20.91 | 12.7 | 33.61 | 38.41 | 38.41 | 95.4825 | 94.8374 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 10.6 | #REF! | 45.62 | 37.83 | 83.45 | 94.05 | 47.025 | 94.3918 | 93.6794 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 13.0409 | #REF! | 18.43 | 3.28 | 21.71 | 34.7509 | 11.5836 | 99.0273 | 98.4431 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 15.121 | #REF! | 84.34 | 15.2 | 99.54 | 114.661 | 22.9322 | 97.3242 | 96.9177 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 2.0687 | #REF! | 4.43 | 0.4 | 4.83 | 6.8987 | 6.8987 | 99.3508 | 99.0727 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 17.5 | #REF! | 170.35 | 35.8 | 206.15 | 223.65 | 31.95 | 96.0417 | 95.7056 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 21.45 | #REF! | 129.25 | 52.2 | 181.45 | 202.9 | 18.4455 | 97.7829 | 97.5208 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 23.42 | #REF! | 144.25 | 24.83 | 169.08 | 192.5 | 24.0625 | 97.1593 | 96.7658 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 1.5 | #REF! | 35.5 | 23.5 | 59 | 60.5 | 15.125 | 98.0175 | 97.9671 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 157 | #REF! | 119 | 81 | 200 | 357 | 11.9 | 99.1039 | 98.4005 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 57.05 | #REF! | 62.25 | 50 | 112.25 | 169.3 | 11.2867 | 98.9942 | 98.483 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 44.15 | #REF! | 74.65 | 59.35 | 134 | 178.15 | 14.8458 | 98.4991 | 98.0046 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 49 | 49 | 191.9 | #REF! | 1372.7167 | 1579.65 | 2952.3667 | 3144.2667 | 64.1687 | 91.9016 | 91.3752 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 361.08 | #REF! | 2045.2067 | 1913.42 | 3958.6267 | 4319.7067 | 73.2154 | 90.9818 | 90.1592 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 210.5 | #REF! | 480.87 | 302.97 | 783.84 | 994.34 | 20.7154 | 97.8051 | 97.2157 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 52.3 | #REF! | 241.3 | 61.83 | 303.13 | 355.43 | 9.8731 | 98.8682 | 98.673 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 64.75 | #REF! | 128.2272 | 37.1889 | 165.4161 | 230.1661 | 8.8525 | 99.1449 | 98.8101 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 60.3236 | #REF! | 60.3236 | 17.9618 | 78.2854 | 138.609 | 1.0914 | 99.9171 | 99.8533 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 1.32 | #REF! | 1.4576 | 0.25764 | 1.7153 | 3.0353 | 0.12647 | 99.9904 | 99.983 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 16.15 | #REF! | 13.6972 | 6.8778 | 20.575 | 36.725 | 5.2464 | 99.6049 | 99.2948 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 5.0508 | #REF! | 7.116 | 2.7389 | 9.8549 | 14.9057 | 0.67753 | 99.9398 | 99.9089 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
Note: The Outage due to incoming supply failure for Devanahlli has been confirmed as Zero from concerned circle for the month of Aug-16
|  | 516 | 516 | 1344.085 | #REF! | 5604.895 | 4641.085 | 10245.98 | 11590.065 | 547.8533 | 97.2421 | 96.8804 | #REF! | #REF! | #REF! | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
Devanahalli
| Hosakote |  |  |  |  | 114.07 | 34.45
Nelamangala
Doddaballapura
Bangalore South
#NAME?
52.4382
98.4167
|  | 2 | 2 | 8
|  | 5 | 5 | 12
|  | 7 | 7 | 18
|  | 2 | 2 | 22
|  | 2 | 2 | 25
|  | 2 | 2 | 42
|  | 4 | 4 | 105 |  |  |  | 20000
|  | 1 | 1 | 54 |  |  |  | 5000
|  | 1 | 1 | 91 |  |  |  | 5000
8000
18000
2000
[11 empty] | 2535.6241 | 2526.3638 |  |  | #REF! | #REF! | #VALUE!
[11 empty] | 97.524 | 97.1678 |  |  | #REF! | #REF!

## Jan ANX III (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
C. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Jan-2017 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Jan-2017 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 230 | 227 | 88.33 | 1496.89 | 4156.66 | 1092.83 | 5249.49 | 5337.82 | 23.2079 | 95.9097 | 95.8409 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 172 | 172 | 26.46 | 776.38 | 3454.65 | 799.94 | 4254.59 | 4281.05 | 24.8898 | 95.567 | 95.5395 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 135.25 | 1442.56 | 3364.52 | 3697.68 | 7062.2 | 7197.45 | 40.4351 | 92.8897 | 92.7536 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 192 | 192 | 53.2 | 461.2546 | 1919.05 | 637.23 | 2556.28 | 2609.48 | 13.591 | 97.614 | 97.5643 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 365 | 58 | 864.6 | 4034.65 | 4919.2 | 8953.85 | 9011.85 | 23.4074 | 95.8321 | 95.8051 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.96667
6 | Tiptur | 187 | 187 | 62 | 869.45 | 2597.75 | 3252.8 | 5850.55 | 5912.55 | 31.6179 | 94.3931 | 94.3337 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.0333
7 | Madhugiri | 289 | 289 | 64 | 740.41 | 3804.75 | 1929.17 | 5733.92 | 5797.92 | 20.062 | 96.4443 | 96.4047 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.0667
8 | Kolar | 134 | 134 | 50.4 | #REF! | 248.77 | 231.73 | 480.5 | 530.9 | 3.9619 | 99.3574 | 99.29 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 170 | 170 | 209 | #REF! | 455 | 132 | 587 | 796 | 4.6824 | 99.3812 | 99.1609 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.4833
10 | CB Pura | 173 | 173 | 1267.2 | #REF! | 785.54 | 652.25 | 1437.79 | 2704.99 | 15.6358 | 98.5106 | 97.1979 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 21.12
11 | Chintamani | 120 | 120 | 70.3 | #REF! | 873.57 | 493.82 | 1367.39 | 1437.69 | 11.9808 | 97.9579 | 97.8529 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 56.5 | #REF! | 451.32 | 129.67 | 580.99 | 637.49 | 18.7497 | 96.9376 | 96.6398 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 92.99 | #REF! | 511.27 | 336.83 | 848.1 | 941.09 | 30.3577 | 95.0971 | 94.5595 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 149.49 | #REF! | 962.59 | 466.5 | 1429.09 | 1578.58 | 24.2858 | 96.0599 | 95.6477 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 12 | #REF! | 95.85 | 141.08 | 236.93 | 248.93 | 17.7807 | 96.9671 | 96.8135 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 24.25 | #REF! | 114.35 | 410.23 | 524.58 | 548.83 | 15.6809 | 97.314 | 97.1898 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 132.65 | #REF! | 117.4 | 109.3 | 226.7 | 359.35 | 8.9838 | 98.9843 | 98.39 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 168.9 | #REF! | 327.6 | 660.61 | 988.21 | 1157.11 | 13.0012 | 98.0101 | 97.67 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.41 | #REF! | 5.709 | 2.4972 | 8.2063 | 8.6163 | 0.45349 | 99.9226 | 99.9187 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 16.17 | #REF! | 61.3458 | 74.6211 | 135.9669 | 152.1369 | 4.4746 | 99.2833 | 99.1981 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 94.71 | #REF! | 55.0204 | 97.7033 | 142.2364 | 236.9464 | 5.0414 | 99.4577 | 99.0965 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 110.88 | #REF! | 116.3662 | 172.3244 | 288.6907 | 399.5707 | 4.933 | 99.3613 | 99.116 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 6.681 | #REF! | 35.0882 | 12.066 | 47.1542 | 53.8351 | 0.84117 | 99.868 | 99.8493 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note : * Total No of 11KV Feeders pertaining to Madhugiri Division under Annexure-3 is 289 including Newly comissioned NJY feeders under Phase-3 (earlier 272 feeders). * Total No of 11KV Feeders pertaining to Davanagere Division under Annexure-3 is 230 including Newly comissioned NJY feeder under Phase-3 (earlier 229 feeders).
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
|  |  | 123.9 |  | 41.659 | 85.7965 | [10 empty] | 0
|  |  | 8.75 |  | 75.74 | 23.58 |  | 114.35 | 410.23 | [7 empty] | 0
[15 empty] | 98.57 | 97.92 | -98.57
[7 empty] | 3.42 | [9 empty] | 0
[7 empty] | 0.47 | [9 empty] | 0
0
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1947.6888 | 1943.3987
|  | 2548 | [8 empty] | 97.3844 | 97.1699
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2548
|  | 1420 | [7 empty] | 4836.58 |  |  |  |  | #REF! | #REF!
529
4497
138.87

## Feb ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Feb'17 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Feb-2017 |  |  |  | Reliability for cumulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 4.13 | #REF! | 113.51 | 42.18 | 155.69 | 159.82 | 4.7006 | 99.3186 | 99.3005 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 11.5 | #REF! | 207.57 | 158.47 | 366.04 | 377.54 | 34.3218 | 95.0482 | 94.8926 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 65 | #REF! | 251 | 58 | 309 | 374 | 12.4667 | 98.4673 | 98.1448 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1347 | 1089 | 689.44 | #REF! | 3671.37 | 4448 | 8119.37 | 8808.81 | 6.5396 | 99.103 | 99.0268 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 0.25 | #REF! | 6.75 | 7.25 | 14 | 14.25 | 3.5625 | 99.4792 | 99.4699 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 13 | 13 | 2.3 | #REF! | 26.24 | 31.45 | 57.69 | 59.99 | 4.6146 | 99.3396 | 99.3133 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 4.5 | #REF! | 120.5 | 36 | 156.5 | 161 | 17.8889 | 97.4124 | 97.338 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1444 | 783.44 | #REF! | #REF! | 4491.2 | 4785.9 | 9277.1 | 10056.42 | 97.3689 | 99.1365 | 99.0639 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
Note: | A new feeder commissioned in Bangalore Urban South Circle : F10 feeder, Anjanapura MUSS,
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
113.52

## Feb ANX II (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
B. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Feb-2017 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  |  |  | Reliability for Feb-2017 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage |  |  | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 |  |  | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 1.45 | #REF! | 12.2 | 2.05 |  |  | 14.25 | 15.7 | 15.7 | 97.8795 | 97.6637 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
2 | Channagiri | 1 | 1 | 6.35 | #REF! | 23.55 | 0.1 |  |  | 23.65 | 30 | 30 | 96.4807 | 95.5357 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
3 | Harihara | 11 | 11 | 0.35 | #REF! | 91.11 | 26.55 |  |  | 117.66 | 118.01 | 10.7282 | 98.4083 | 98.4035 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
4 | Honnali | 2 | 2 | 1.05 | #REF! | 42.25 | 3.2 |  |  | 45.45 | 46.5 | 23.25 | 96.6183 | 96.5402 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
5 | Harapanahalli | 4 | 4 | 0.15 | #REF! | 27.35 | 1.3 |  |  | 28.65 | 28.8 | 7.2 | 98.9342 | 98.9286 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
6 | Holalkere | 1 | 1 | 5 | #REF! | 21.33 | 13.38 |  |  | 34.71 | 39.71 | 39.71 | 94.8348 | 94.0908 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
7 | Hosadurga | 2 | 2 | 10.2 | #REF! | 46.47 | 38.4 |  |  | 84.87 | 95.07 | 47.535 | 93.6853 | 92.9263 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
8 | Hiriyur | 3 | 3 | 13.1713 | #REF! | 13.15 | 2.2 |  |  | 15.35 | 28.5213 | 9.5071 | 99.2386 | 98.5853 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
9 | Challakere | 5 | 5 | 15.2722 | #REF! | 9.13 | 8.18 |  |  | 17.31 | 32.5822 | 6.5164 | 99.4848 | 99.0303 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
10 | Molakalmuru | 1 | 1 | 2.0894 | #REF! | 4.35 | 0.4 |  |  | 4.75 | 6.8394 | 6.8394 | 99.2932 | 98.9822 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
11 | Tumkur | 7 | 7 | 10.35 | #REF! | 119.85 | 43.8 | 120.25 | 45.2 | 163.65 | 174 | 24.8571 | 96.521 | 96.301 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
12 | Tiptur | 11 | 11 | 13.25 | #REF! | 125.1 | 47.05 | 126.5 | 48.45 | 172.15 | 185.4 | 16.8545 | 97.6711 | 97.4919 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
13 | Madhugiri | 8 | 8 | 10.85 | #REF! | 120.17 | 16.81 | 120.57 | 17.21 | 136.98 | 147.83 | 18.4787 | 97.452 | 97.2502 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
14 | Srinivaspura | 4 | 4 | 3.5 | #REF! | 18.4 | 31.01 |  |  | 49.41 | 52.91 | 13.2275 | 98.1618 | 98.0316 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
15 | KGF | 30 | 30 | 192 | #REF! | 73 | 113 |  |  | 186 | 378 | 12.6 | 99.0774 | 98.125 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
16 | CB Pura | 15 | 15 | 77.55 | #REF! | 112.36 | 123.1 |  |  | 235.46 | 313.01 | 20.8673 | 97.6641 | 96.8947 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
17 | Chintamani | 12 | 12 | 46.45 | #REF! | 163.55 | 58.68 |  |  | 222.23 | 268.68 | 22.39 | 97.2442 | 96.6682 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
18 | Devanahalli | 50 | 50 | 38.8 | #REF! | 1185.1 | 735 |  |  | 1920.1 | 1958.9 | 39.178 | 94.2854 | 94.1699 | #REF! | #REF! | #REF! | #REF! | Devanahalli | #REF! | #REF!
19 | Hosakote | 59 | 59 | 50.2625 | #REF! | 1396.4368 | 168.55 |  |  | 1564.9868 | 1615.2493 | 27.3771 | 96.0528 | 95.926 | #REF! | #REF! | #REF! | #REF! | Hosakote | #REF! | #REF!
20 | Nelamangala | 48 | 48 | 243.59 | #REF! | 558.44 | 214 |  |  | 772.44 | 1016.03 | 21.1673 | 97.6053 | 96.8501 | #REF! | #REF! | #REF! | #REF! | Nelamangala | #REF! | #REF!
21 | Doddaballapura | 36 | 36 | 31 | #REF! | 245.25 | 77.85 |  |  | 323.1 | 354.1 | 9.8361 | 98.6644 | 98.5363 | #REF! | #REF! | #REF! | #REF! | Doddaballapura | #REF! | #REF!
22 | Magadi | 26 | 26 | 54.15 | #REF! | 230.01 | 20.53 | 230.41 | 20.53 | 250.54 | 304.69 | 11.7188 | 98.566 | 98.2561 | #REF! | #REF! | #REF! | #REF! | Magadi | #REF! | #REF!
23 | Anekal | 127 | 127 | 55.34 | #REF! | 55.34 | 14.48 |  |  | 69.82 | 125.16 | 0.98551 | 99.9182 | 99.8533 | #REF! | #REF! | #REF! | #REF! | Anekal | #REF! | #REF!
24 | Ramanagara | 24 | 24 | 3.66 | #REF! | 16.57 | 8.4042 |  |  | 24.9742 | 28.6342 | 1.1931 | 99.8452 | 99.8225 | #REF! | #REF! | #REF! | #REF! | Ramanagara | #REF! | #REF!
25 | Channapatna | 7 | 7 | 0.38 | #REF! | 26.48 | 1.56 |  |  | 28.04 | 28.42 | 4.06 | 99.4039 | 99.3958 | #REF! | #REF! | #REF! | #REF! | Channapatna | #REF! | #REF!
26 | Kanakapura | 22 | 22 | 5.0508 | #REF! | 6.56 | 0.52639 |  |  | 7.0864 | 12.1372 | 0.55169 | 99.9521 | 99.9179 | #REF! | #REF! | #REF! | #REF! | Kanakapura | #REF! | #REF!
Note: A feeder is newly commissioned in Devanahalli Division, Feeder name:F-12 Kundana ( Pandithapura Station)
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
Devanahalli
| Hosakote |  |  |  |  | 114.07 | 34.45 | 242.8 | 77.85
Nelamangala
Doddaballapura
Bangalore South
#NAME?
52.4382
98.4167
|  | 2 | 2 | 8
|  | 5 | 5 | 12
|  | 7 | 7 | 18
|  | 2 | 2 | 22
|  | 2 | 2 | 25
|  | 2 | 2 | 42
|  | 4 | 4 | 105 | [5 empty] | 20000
|  | 1 | 1 | 54 | [5 empty] | 5000
|  | 1 | 1 | 91 | [5 empty] | 5000
8000
18000
2000
[13 empty] | 2542.9425 | 2534.1772 |  |  | #REF! | #REF! | #VALUE!
[13 empty] | 97.8055 | 97.4684 |  |  | #REF! | #REF!

## Feb ANX III (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
C. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Feb-2017 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Feb-2017 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 236 | 233 | 195.2 | 1692.09 | 5282.5447 | 1355.24 | 6637.7847 | 6832.9847 | 28.9533 | 94.4194 | 94.2553 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 172 | 172 | 13.28 | 789.66 | 3170.29 | 834.35 | 4004.64 | 4017.92 | 23.36 | 95.3804 | 95.3651 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 120.5 | 1563.06 | 3440.17 | 3748.41 | 7188.58 | 7309.08 | 41.0622 | 91.987 | 91.8527 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 194 | 194 | 51.39 | 512.6446 | 1758.024 | 388.08 | 2146.104 | 2197.494 | 11.3273 | 97.8051 | 97.7525 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 385 | 65 | 929.6 | 4103.15 | 3368.2 | 7471.35 | 7536.35 | 19.5749 | 96.1496 | 96.1161 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.0833
6 | Tiptur | 187 | 187 | 54 | 923.45 | 1759 | 2407 | 4166 | 4220 | 22.5668 | 95.5797 | 95.5225 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.9
7 | Madhugiri | 289 | 289 | 62 | 802.41 | 3960 | 1593 | 5553 | 5615 | 19.4291 | 96.1876 | 96.145 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.0333
8 | Kolar | 134 | 134 | 50.42 | #REF! | 1121.15 | 915.06 | 2036.21 | 2086.63 | 15.5719 | 96.985 | 96.9103 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 170 | 170 | 230 | #REF! | 150 | 410 | 560 | 790 | 4.6471 | 99.3464 | 99.078 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.8333
10 | CB Pura | 175 | 175 | 2043 | #REF! | 2317.32 | 3032.17 | 5349.49 | 7392.49 | 42.2428 | 93.9348 | 91.6185 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 34.05
11 | Chintamani | 120 | 120 | 31.15 | #REF! | 1461.1 | 517.35 | 1978.45 | 2009.6 | 16.7467 | 96.7288 | 96.6772 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 35 | #REF! | 451.25 | 172.6167 | 623.8667 | 658.8667 | 19.3784 | 96.3593 | 96.1551 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 45.025 | #REF! | 499.2581 | 220.5369 | 719.795 | 764.82 | 24.6716 | 95.393 | 95.1048 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 80.03 | #REF! | 950.51 | 393.15 | 1343.66 | 1423.69 | 21.9029 | 95.8985 | 95.6542 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 65.71 | #REF! | 95.85 | 141.08 | 236.93 | 302.64 | 21.6171 | 96.6421 | 95.7109 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 50.75 | #REF! | 114.35 | 410.23 | 524.58 | 575.33 | 16.438 | 97.0262 | 96.7385 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 123.9 | #REF! | 121.64 | 75.68 | 197.32 | 321.22 | 8.0305 | 99.0212 | 98.4066 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 240.36 | #REF! | 331.84 | 626.99 | 958.83 | 1199.19 | 13.474 | 97.8624 | 97.3266 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.14514 | #REF! | 7.3889 | 3.0569 | 10.4458 | 10.591 | 0.55742 | 99.8909 | 99.8894 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 3.59 | #REF! | 33.58 | 5.5111 | 39.0911 | 42.6811 | 1.2553 | 99.7719 | 99.7509 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 78.59 | #REF! | 62.4264 | 33.9993 | 142.2364 | 220.8264 | 4.6984 | 99.3995 | 99.0678 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 82.18 | #REF! | 96.01 | 39.51 | 135.52 | 217.7 | 2.6877 | 99.668 | 99.4667 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 6.58 | #REF! | 51.55 | 11.0326 | 62.5826 | 69.1626 | 1.0807 | 99.806 | 99.7856 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: 1) 6 NJY Feeders are newly commissioned in Davanagere Division. Hiremallanahole - 2, Bilichodu-2, Mellekatte-2 Nos. 2) 2 NJY Feeders are newly commissioned in Hiriyur Division, Chigalikatte feeder-1(Hinduskatte MUSS), Lakshmi pura feeder(Ranganathapura MUSS) 3) 2 Feeders are newly commissioned in CB Pura Division F11 vapasandra( Guddibanda MUSS) & F10 Pesalaparathi( Thimmampalli MUSS)
Note : * Total No of 11KV Feeders pertaining to Madhugiri Division under Annexure-3 is 289 including Newly comissioned NJY feeders under Phase-3 (earlier 272 feeders). * Total No of 11KV Feeders pertaining to Davanagere Division under Annexure-3 is 230 including Newly comissioned NJY feeder under Phase-3 (earlier 229 feeders).
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
|  |  | 123.9 |  | 41.659 | 85.7965 | [10 empty] | 0
|  |  | 8.75 |  | 75.74 | 23.58 |  | 114.35 | 410.23 | [7 empty] | 0
[15 empty] | 98.57 | 97.92 | -98.57
[7 empty] | 3.42 | [9 empty] | 0
[7 empty] | 0.47 | [9 empty] | 0
Note: 1) 6 NJY Feeders are newly commissioned in Davanagere Division. Hiremallanahole - 2, Bilichodu-2, Mellekatte-2 Nos. 2) 2 NJY Feeders are newly commissioned in Hiriyur Division, 1) Hinduskatte Station Chigalikatte Feeder 2) Ranganathapura Station Laxmipura Feeder
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1937.8141 | 1931.9029
|  | 2558 | [8 empty] | 96.8907 | 96.5951
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2558
|  | 1420 | [7 empty] | 4681.69 |  |  |  |  | #REF! | #REF!
529
4507
138.87
Note: Newly added feeders in the month of february-2017 F11 Vapasandra of Gudibanda MUSS and F-10 Pesalaparthi of Thimmampalli MUSS

## Mar ANX I (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR Mar'17 OF FY 2016-17 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Mar-2017 |  |  |  | Reliability for cumulative period From April-16 | [6 empty] | 2016-08-01 | 31 | 31
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31
1 | Davangere | 34 | 31 | 4.38 | #REF! | 35.27 | 26.52 | 61.79 | 66.17 | 1.9462 | 99.7557 | 99.7384 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-11-01 | 30 | 30 | 153
2 | Chitradurga | 11 | 11 | 10.25 | #REF! | 208.28 | 159.2 | 367.48 | 377.73 | 34.3391 | 95.5098 | 95.3845 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-12-01 | 31 | 31
3 | Tumkur | 30 | 30 | 54 | #REF! | 246 | 50 | 296 | 350 | 11.6667 | 98.6738 | 98.4319 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-01-01 | 31 | 31
4 | Bangalore Urban | 1351 | 1163 | 701.46 | #REF! | 4477.13 | 6808.41 | 11285.54 | 11987 | 8.8727 | 98.8772 | 98.8074 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-02-01 | 29 | 29
5 | Ramanagara | 4 | 4 | 1 | #REF! | 6.09 | 7.4 | 13.49 | 14.49 | 3.6225 | 99.5467 | 99.5131 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | 2016-03-01 | 31 | 31
6 | Kolar | 13 | 13 | 1.3 | #REF! | 39.09 | 7.24 | 46.33 | 47.63 | 3.6638 | 99.521 | 99.5075 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  | 366 | 0
7 | CBPura | 9 | 9 | 44.3 | #REF! | 175.05 | 98.38 | 273.43 | 317.73 | 35.3033 | 95.9165 | 95.2549 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
|  | 1448 | 795.46 | #REF! | #REF! | 5322.87 | 7248.29 | 12571.16 | 13430.85 | 131.0538 | 98.8331 | 98.7533 | #REF! | #REF! | #REF! | #REF! |  |  | #REF!
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | #REF! | #REF! | #REF! |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | #REF! | #REF! |  |  | #REF!
[15 empty] | #REF! | #REF! |  |  | #REF!
0
0
0
0
0
0
Note: | Four new feeders added in BMAZ 1. South circle:F11 feeder, Arehalli MUSS 2. East circle: F-16 feeder in HBR 3. East circle: F-19 feeder in Manyatha MUSS 4. North circle: F-4 feeder in Brindavan MUSS
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation
[12 empty] | 35.27 | 26.52
[12 empty] | 208.28 | 159.2
[12 empty] | 246 | 50
113.52
[12 empty] | 39.09 | 7.24
[12 empty] | 175.05 | 98.38

## Mar ANX II (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
B. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR Mar-2017 OF FY 2016-17
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  |  |  | Reliability for Mar-2017 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage |  |  | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 |  |  | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Jagalur | 1 | 1 | 10.4 | #REF! | 8.05 | 3.1 |  |  | 11.15 | 21.55 | 21.55 | 98.5013 | 97.1035 | 119.4295 | 119.4295 | 98.7554 | 98.6366 |  | -0.25403 | -1.5332
2 | Channagiri | 1 | 1 | 7.45 | #REF! | 20.15 | 1.45 |  |  | 21.6 | 29.05 | 29.05 | 97.0968 | 96.0954 | 125.5307 | 125.5307 | 98.652 | 98.567 |  | -1.5553 | -2.4716
3 | Harihara | 11 | 11 | 1.1 | #REF! | 70.31 | 8.2 |  |  | 78.51 | 79.61 | 7.2373 | 99.0407 | 99.0272 | 178.0183 | 16.1835 | 99.8164 | 99.8153 |  | -0.77571 | -0.78801
4 | Honnali | 2 | 2 | 1.25 | #REF! | 38.15 | 3 |  |  | 41.15 | 42.4 | 21.2 | 97.2345 | 97.1505 | 139.0183 | 69.5092 | 99.2137 | 99.2065 |  | -1.9791 | -2.056
5 | Harapanahalli | 4 | 4 | 0.25 | #REF! | 2.1 | 2.25 |  |  | 4.35 | 4.6 | 1.15 | 99.8538 | 99.8454 | 103.5342 | 25.8835 | 99.7052 | 99.7045 |  | 0.14859 | 0.1409
6 | Holalkere | 1 | 1 | 5.12 | #REF! | 21.36 | 13.05 |  |  | 34.41 | 39.53 | 39.53 | 95.375 | 94.6868 | 134.3648 | 134.3648 | 98.5246 | 98.4662 |  | -3.1496 | -3.7793
7 | Hosadurga | 2 | 2 | 12.55 | #REF! | 46.52 | 38.53 |  |  | 85.05 | 97.6 | 48.8 | 94.2843 | 93.4409 | 191.2853 | 95.6426 | 98.9798 | 98.9082 |  | -4.6955 | -5.4673
8 | Hiriyur | 3 | 3 | 13.5006 | #REF! | 16.06 | 2.08 |  |  | 18.14 | 31.6406 | 10.5469 | 99.1873 | 98.5824 | 130.8791 | 43.6264 | 99.5534 | 99.502 |  | -0.36608 | -0.91957
9 | Challakere | 5 | 5 | 16.05 | #REF! | 26.07 | 11.21 |  |  | 37.28 | 53.33 | 10.666 | 98.9978 | 98.5664 | 152.8148 | 30.563 | 99.6878 | 99.6511 |  | -0.6899 | -1.0847
10 | Molakalmuru | 1 | 1 | 2.1417 | #REF! | 5.1 | 0.2 |  |  | 5.3 | 7.4417 | 7.4417 | 99.2876 | 98.9998 | 106.7348 | 106.7348 | 98.806 | 98.7816 |  | 0.48162 | 0.21821
11 | Tumkur | 7 | 7 | 15 | #REF! | 124 | 45 | 120.25 | 45.2 | 169 | 184 | 26.2857 | 96.755 | 96.467 | 280.521 | 40.0744 | 99.567 | 99.5425 |  | -2.812 | -3.0756
12 | Tiptur | 11 | 11 | 17 | #REF! | 121 | 49 | 126.5 | 48.45 | 170 | 187 | 17 | 97.9228 | 97.7151 | 284.6711 | 25.8792 | 99.7222 | 99.7046 |  | -1.7994 | -1.9895
13 | Madhugiri | 8 | 8 | 15 | #REF! | 127.22 | 63.08 | 120.57 | 17.21 | 190.3 | 205.3 | 25.6625 | 96.8028 | 96.5507 | 302.752 | 37.844 | 99.5894 | 99.568 |  | -2.7866 | -3.0173
14 | Srinivaspura | 4 | 4 | 1.3 | #REF! | 15.05 | 28.55 |  |  | 43.6 | 44.9 | 11.225 | 98.5349 | 98.4913 | 143.0618 | 35.7655 | 99.5954 | 99.5917 |  | -1.0605 | -1.1005
15 | KGF | 30 | 30 | 169 | #REF! | 60 | 119 |  |  | 179 | 348 | 11.6 | 99.198 | 98.4409 | 447.0774 | 14.9026 | 99.8942 | 99.8299 |  | -0.69616 | -1.389
16 | CB Pura | 15 | 15 | 86.5 | #REF! | 91.33 | 43.2 |  |  | 134.53 | 221.03 | 14.7353 | 98.7945 | 98.0194 | 318.6941 | 21.2463 | 99.8233 | 99.7575 |  | -1.0288 | -1.738
17 | Chintamani | 12 | 12 | 26.51 | #REF! | 211.27 | 105.5 |  |  | 316.77 | 343.28 | 28.6067 | 96.4519 | 96.155 | 440.5242 | 36.7103 | 99.6062 | 99.5809 |  | -3.1542 | -3.4259
18 | Devanahalli | 50 | 50 | 188.25 | #REF! | 1590.23 | 1849.2 |  |  | 3439.43 | 3627.68 | 72.5536 | 90.7542 | 90.2482 | 3721.9654 | 74.4393 | 99.1932 | 99.1502 | Devanahalli | -8.439 | -8.9021
19 | Hosakote | 59 | 59 | 417.31 | #REF! | 2725.04 | 2441.31 |  |  | 5166.35 | 5583.66 | 94.6383 | 88.2305 | 87.2798 | 5679.7128 | 96.2663 | 98.9818 | 98.9011 | Hosakote | -10.7513 | -11.6213
20 | Nelamangala | 48 | 48 | 237.09 | #REF! | 466.3 | 408.3 |  |  | 874.6 | 1111.69 | 23.1602 | 97.551 | 96.8871 | 1209.2953 | 25.1937 | 99.7688 | 99.7124 | Nelamangala | -2.2178 | -2.8253
21 | Doddaballapura | 36 | 36 | 208.2 | #REF! | 405.25 | 143.55 |  |  | 548.8 | 757 | 21.0278 | 97.951 | 97.1737 | 855.6644 | 23.7685 | 99.7947 | 99.7287 | Doddaballapura | -1.8437 | -2.555
22 | Magadi | 26 | 26 | 97.18 | #REF! | 202.2 | 59 | 230.41 | 20.53 | 261.2 | 358.38 | 13.7838 | 98.6497 | 98.1473 | 456.946 | 17.5748 | 99.842 | 99.7994 | Magadi | -1.1923 | -1.652
23 | Anekal | 127 | 127 | 55.0438 | #REF! | 55.0438 | 24.4854 |  |  | 79.5292 | 134.5729 | 1.0596 | 99.9158 | 99.8576 | 234.4911 | 1.8464 | 99.9839 | 99.9789 | Anekal | -0.068039 | -0.12135
24 | Ramanagara | 24 | 24 | 0.54 | #REF! | 9.6819 | 1.9215 |  |  | 11.6035 | 12.1435 | 0.50598 | 99.935 | 99.932 | 111.9886 | 4.6662 | 99.947 | 99.9467 | Ramanagara | -0.011973 | -0.014741
25 | Channapatna | 7 | 7 | 0.42 | #REF! | 19.6597 | 5.2625 |  |  | 24.9222 | 25.3422 | 3.6203 | 99.5215 | 99.5134 | 124.7461 | 17.8209 | 99.7973 | 99.7966 | Channapatna | -0.27579 | -0.28317
26 | Kanakapura | 22 | 22 | 5.02 | #REF! | 7.8076 | 1.9708 |  |  | 9.7785 | 14.7985 | 0.67266 | 99.9403 | 99.9096 | 114.7505 | 5.2159 | 99.9431 | 99.9405 | Kanakapura | -0.0028036 | -0.030868
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month)
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month)
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
1848.8
| Devanahalli | [8 empty] | 2441.31
| Hosakote |  |  |  |  | 114.07 | 34.45 | 242.8 | 77.85 | 407.85
| Nelamangala | [8 empty] | 143.55
Doddaballapura
Bangalore South
#NAME?
56.6
1.9708
52.4382
98.4167
|  | 2 | 2 | 8
|  | 5 | 5 | 12
|  | 7 | 7 | 18
|  | 2 | 2 | 22
|  | 2 | 2 | 25
|  | 2 | 2 | 42
|  | 4 | 4 | 105 | [5 empty] | 20000
|  | 1 | 1 | 54 | [5 empty] | 5000
|  | 1 | 1 | 91 | [5 empty] | 5000
8000
18000
2000
[13 empty] | 2535.7682 | 2524.2864 |  |  | 2586.7436 | 2585.7685 | #VALUE!
[13 empty] | 97.5295 | 97.0879 |  |  | 99.4901 | 99.4526

## MAR ANX III (hidden)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
C. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR Mar-2017 OF FY 2016-17
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Mar-2017 |  |  |  | Reliability for cumulative period From April-16
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) | Cumulative outage duration of all feeders (In Hrs/Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Davangere | 236 | 233 | 276.44 | 1968.53 | 4222.37 | 2121.15 | 6343.52 | 6619.96 | 28.0507 | 95.1829 | 94.973 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Harihara | 172 | 172 | 118.27 | 907.93 | 4020.24 | 1173.35 | 5193.59 | 5311.86 | 30.8829 | 94.5887 | 94.4654 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Chitradurga | 178 | 178 | 138.25 | 1701.31 | 3445.16 | 3760.16 | 7205.32 | 7343.57 | 41.256 | 92.7456 | 92.6064 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Hiriyur | 194 | 194 | 52.0127 | 564.6573 | 2117.02 | 562 | 2679.02 | 2731.0327 | 14.0775 | 97.5252 | 97.4772 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Tumkur | 385 | 385 | 56 | 985.6 | 5176 | 6453 | 11629 | 11685 | 30.3506 | 94.5869 | 94.5608 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.93333
6 | Tiptur | 187 | 187 | 58 | 981.45 | 2232 | 3736 | 5968 | 6026 | 32.2246 | 94.2806 | 94.225 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.96667
7 | Madhugiri | 299 | 299 | 59 | 861.41 | 5480.18 | 2295.32 | 7775.5 | 7834.5 | 26.2023 | 95.3396 | 95.3042 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.98333
8 | Kolar | 134 | 134 | 60.3 | #REF! | 1021.39 | 992.93 | 2014.32 | 2074.62 | 15.4822 | 97.3061 | 97.2254 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | KGF | 172 | 133 | 387 | #REF! | 110 | 506 | 616 | 1003 | 5.8314 | 99.3582 | 98.9549 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 6.45
10 | CB Pura | 182 | 182 | 1233.5 | #REF! | 1910.25 | 2140.29 | 4050.54 | 5284.04 | 29.0332 | 96.0115 | 94.7969 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 20.5583
11 | Chintamani | 121 | 121 | 58.11 | #REF! | 1491.3 | 680.3 | 2171.6 | 2229.71 | 18.4274 | 96.7837 | 96.6976 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Devanahalli | 34 | 34 | 175.15 | #REF! | 496.07 | 493.32 | 989.39 | 1164.54 | 34.2512 | 94.785 | 93.8618 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Hosakote | 31 | 31 | 237.54 | #REF! | 604.4667 | 683.02 | 1287.4867 | 1525.0267 | 49.1944 | 92.557 | 91.1838 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | Yelahanka | 65 | 65 | 412.29 | #REF! | 1100.1333 | 1175.5333 | 2275.6667 | 2687.9567 | 41.3532 | 93.7258 | 92.589 | #REF! | #REF! | #REF! | #REF!
14 | Nelamangala | 14 | 14 | 65.71 | #REF! | 123.29 | 108.31 | 231.6 | 297.31 | 21.2364 | 97.0353 | 96.1942 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Doddaballapura | 35 | 35 | 35.7 | #REF! | 176.3 | 545.1 | 721.4 | 757.1 | 21.6314 | 96.3062 | 96.1234 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Magadi | 40 | 40 | 371.44 | #REF! | 224.34 | 177.35 | 401.69 | 773.13 | 19.3283 | 98.2003 | 96.5362 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | Nelamangala | 89 | 89 | 473.25 | #REF! | 523.53 | 830.36 | 1353.89 | 1827.14 | 20.5297 | 97.2738 | 96.3208 | #REF! | #REF! | #REF! | #REF!
14 | Chandapura | 19 | 19 | 0.14 | #REF! | 6.109 | 3.2181 | 9.3271 | 9.4671 | 0.49827 | 99.912 | 99.9107 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | Ramanagara | 34 | 34 | 1.74 | #REF! | 33.3 | 20.4875 | 53.7875 | 55.5275 | 1.6332 | 99.7165 | 99.7073 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | Channapatna | 47 | 47 | 1.33 | #REF! | 41 | 39.1368 | 142.2364 | 143.5664 | 3.0546 | 99.4577 | 99.4526 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | Ramanagara | 81 | 81 | 3.07 | #REF! | 74.6312 | 59.6243 | 134.2556 | 137.3256 | 1.6954 | 99.703 | 99.6962 | #REF! | #REF! | #REF! | #REF!
16 | Kanakapura | 64 | 64 | 6.58 | #REF! | 63.5 | 24.1 | 87.6 | 94.18 | 1.4716 | 99.7547 | 99.7363 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: In Madhugiri Division 10Nos. of 11Kv Feeders are newly commissioned In KGF Division 2 Nos of 11KV Feeders are newly Commissioned In CB Pura 7 Nos of 11KV Feeders are newly commissioned In Chintamani 1 No of 11Kv Feeder is newly commissioned
Note : * Total No of 11KV Feeders pertaining to Madhugiri Division under Annexure-3 is 289 including Newly comissioned NJY feeders under Phase-3 (earlier 272 feeders). * Total No of 11KV Feeders pertaining to Davanagere Division under Annexure-3 is 230 including Newly comissioned NJY feeder under Phase-3 (earlier 229 feeders).
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0
0
0
0
|  |  | 123.9 |  | 41.659 | 85.7965 | [10 empty] | 0
|  |  | 8.75 |  | 75.74 | 23.58 |  | 114.35 | 410.23 | [7 empty] | 0
[15 empty] | 98.57 | 97.92 | -98.57
[7 empty] | 3.42 | [9 empty] | 0
[7 empty] | 0.47 | [9 empty] | 0
Note: 1) 6 NJY Feeders are newly commissioned in Davanagere Division. Hiremallanahole - 2, Bilichodu-2, Mellekatte-2 Nos. 2) 2 NJY Feeders are newly commissioned in Hiriyur Division, 1) Hinduskatte Station Chigalikatte Feeder 2) Ranganathapura Station Laxmipura Feeder
[10 empty] | 265 | [6 empty] | 0
[10 empty] | 88.3333 | [6 empty] | 0
0
0
0
0
0
|  | #VALUE! | [8 empty] | 1931.4336 | 1923.9932
|  | 2578 | [8 empty] | 96.5717 | 96.1997
[5 empty] | 1131.74 | [9 empty] | #REF! | #REF!
2578
|  | 1420 | [7 empty] | 5945.9567 |  |  |  |  | #REF! | #REF!
529
4527
138.87
Note: Newly added feeders in the month of february-2017 F11 Vapasandra of Gudibanda MUSS and F-10 Pesalaparthi of Thimmampalli MUSS

## Dec ANX1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED | [19 empty] | 2016-04-01 | 30 | 30
Annexure -I Form-I | [19 empty] | 2016-05-01 | 31 | 31
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR DEC-17 OF FY 2017-18 | [19 empty] | 2016-06-01 | 30 | 30
[20 empty] | 2016-07-01 | 31 | 31
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Dec-2017 |  |  |  | Reliability for cummulative period From April-17 | [6 empty] | 2016-08-01 | 31 | 31 | SAIFI & SAIDI of feeders for Dec-2017
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hr:mm:ss) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder Relaibility Index @ 11 KV feeder level in % | Cummulative Relaibility of supply of Power to consumers |  |  |  | 2016-09-01 | 30 | 30 | Total No. of Feeders Interruption | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 2016-10-01 | 31 | 31 | 17 | 18 | 19=17/3 | 20=18/3
1 | Davangere | 35 | 32 | 11:54 | 19:53 | 188:36 | 39:59 | 228:35 | 240:29 | 6:52 | 99.9634 | 99.9615 | 3392:50 | 96:56 | 99.939 | 99.9388 |  | 0.024407 | 0.022717 | 2016-11-01 | 30 | 30 | 513 | 240.49 | 14.6571 | 6.8711
2 | Chitradurga | 11 | 11 | 6:50 | 59:58 | 217:47 | 139:35 | 357:22 | 364:12 | 33:07 | 99.8181 | 99.8146 | 3203:18 | 291:13 | 99.8165 | 99.8162 |  | 0.0015082 | -0.0015787 | 2016-12-01 | 31 | 31 | 562 | 364.2 | 51.0909 | 33.1091
3 | Tumkur | 30 | 30 | 8:00 | 131:10 | 174:13 | 144:19 | 318:31 | 326:31 | 10:53 | 99.9405 | 99.939 | 3553:44 | 118:27 | 99.9254 | 99.9252 |  | 0.015155 | 0.01383 | 2016-01-01 | 31 | 31 | 609 | 326.52 | 20.3 | 10.884
4 | Bangalore Urban | 1380 | 1141 | 478:42 | 7580:55 | 3559:55 | 7256:50 | 10816:45 | 11295:27 | 8:11 | 99.9561 | 99.9542 | 4938.7862 | 85:54 | 99.946 | 99.9458 |  | 0.010109 | 0.0083852 | 2016-02-01 | 29 | 29 | 15054 | 11295.4469 | 10.9087 | 8.1851
5 | Ramanagara | 4 | 4 | 1:20 | 80:59 | 55:29 | 13:49 | 69:18 | 70:38 | 17:40 | 99.903 | 99.9011 | 490:45 | 122:41 | 99.9228 | 99.9225 |  | -0.019786 | -0.021442 | 2016-03-01 | 31 | 31 | 103 | 70.6367 | 25.75 | 17.6592
6 | Kolar | 13 | 13 | 2:22 | 18:14 | 26:43 | 2:38 | 29:21 | 31:43 | 2:26 | 99.9874 | 99.9863 | 282:29 | 21:44 | 99.9864 | 99.9863 |  | 0.69063 | 0.65001 |  | 366 | 0 | 481 | 31.7167 | 37 | 2.4397
7 | CBPura | 9 | 9 | 73:35 | 1698:01 | 124:10 | 35:20 | 159:30 | 233:05 | 25:54 | 99.9007 | 99.855 | 11334:09 | 1259:21 | 99.2101 | 99.205 |  | 0.69063 | 0.65001 |  |  |  | 249 | 233.0833 | 27.6667 | 25.8981
|  | 1478 | 1236 | 27.2472 | 6407:10 | 185.1804 | 319.3832 | 504.5636 | 531.8108 | 5.3544 | 99.9541 | 99.9516 | 5607.0539 | 134.7453 | 99.9428 | 99.9425 |  |  | 0.0091173
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month] | [18 empty] | 0
0
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month] | [18 empty] | 0
0
0
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of | [18 empty] | 0
0
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [18 empty] | 0
0
0
0
0
0
0
95.5714 | [18 empty] | 0
[15 empty] | 299.8023 | 299.7791 | #VALUE! |  | -299.7791
[15 empty] | 99.9341 | 99.9264 |  |  | -99.9264
0
[15 empty] | 199.1561 | 199.1507 |  |  | -199.1507
[15 empty] | 99.5781 | 99.5754 |  |  | -99.5754
0
0
0
0
0
0
0
0
0
0
0
0
[15 empty] | 199.8481 | 199.8478 |  |  | -199.8478
[15 empty] | 99.9241 | 99.9239 |  |  | -99.9239
0
0
0
0
0
0
Note: | Two New feeders were added in BMAZ in the month of Dec-17
| Assistant Executive Engineer(Ele) | [12 empty] | Deputy General Manager(Ele)
| Operation-1 | [12 empty] | Operation-2
Chief General Manager(Ele)
Operation

## Dec ANX11
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
A. RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR DEC-2017 OF FY 2017-18
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Dec-2017 |  |  |  | Reliability for cummulative period From April-17 | [6 empty] | SAIFI & SAIDI of feeders for Dec-2017
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hr:mm:ss) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder Relaibility Index @ 11 KV feeder level in % | Cummulative Relaibility of supply of Power to consumers |  |  |  | Total No. of Feeder Interruptions | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 17 | 18 | 19=17/3 | 20=18/3
1 | Jagalur | 1 | 1 | 9:55 | 84:10 | 1:09 | 0:09 | 1:18 | 11:13 | 11:13 | 99.9927 | 99.9372 | 252:04 | 252:04 | 99.8471 | 99.8409 |  | 0.14559 | 0.096316 | 5 | 11.2167 | 5 | 11.2167
2 | Channagiri | 1 | 1 | 10:25 | 68:55 | 80:18 | 0:27 | 80:45 | 91:10 | 91:10 | 99.5478 | 99.4894 | 422:22 | 422:22 | 99.7399 | 99.7334 |  | -0.19216 | -0.24392 | 82 | 91.1667 | 82 | 91.1667
3 | Harihara | 11 | 11 | 0:30 | 41:05 | 92:02 | 25:48 | 117:50 | 118:20 | 10:45 | 99.94 | 99.9398 | 1201:32 | 109:14 | 99.9311 | 99.931 |  | 0.0089381 | 0.0087122 | 239 | 118.3333 | 21.7273 | 10.7576
4 | Honnali | 2 | 2 | 2:40 | 39:43 | 30:45 | 1:35 | 32:20 | 35:00 | 17:30 | 99.9095 | 99.902 | 433:03 | 216:32 | 99.8641 | 99.8633 |  | 0.045314 | 0.038689 | 109 | 35 | 54.5 | 17.5
5 | Harapanahalli | 4 | 4 | 0:30 | 13:25 | 16:20 | 4:35 | 20:55 | 21:25 | 5:21 | 99.9707 | 99.97 | 367:20 | 91:50 | 99.9421 | 99.942 |  | 0.028611 | 0.02799 | 75 | 21.4167 | 18.75 | 5.3542
6 | Holalkere | 1 | 1 | 2:20 | 26:20 | 23:24 | 10:59 | 34:23 | 36:43 | 36:43 | 99.8074 | 99.7944 | 335:10 | 335:10 | 99.7899 | 99.7884 |  | 0.017563 | 0.0059686 | 60 | 36.7167 | 60 | 36.7167
7 | Hosadurga | 2 | 2 | 4:45 | 54:10 | 36:41 | 28:58 | 65:39 | 70:24 | 35:12 | 99.8162 | 99.8029 | 632:44 | 316:22 | 99.8018 | 99.8003 |  | 0.014397 | 0.0025959 | 101 | 70.4 | 50.5 | 35.2
8 | Hiriyur | 3 | 3 | 4:04 | 16:38 | 19:20 | 7:01 | 26:21 | 30:25 | 10:08 | 99.9508 | 99.9432 | 588:43 | 196:14 | 99.877 | 99.8761 |  | 0.07384 | 0.067091 | 126 | 30.4246 | 42 | 10.1415
9 | Challakere | 5 | 5 | 7:14 | 29:30 | 58:17 | 10:09 | 68:26 | 75:40 | 15:08 | 99.9233 | 99.9153 | 899:44 | 179:57 | 99.8873 | 99.8864 |  | 0.03604 | 0.028855 | 248 | 75.6634 | 49.6 | 15.1327
10 | Molakalmuru | 1 | 1 | 4:36 | 18:47 | 2:45 | 1:02 | 3:47 | 8:23 | 8:23 | 99.9788 | 99.953 | 103:07 | 103:07 | 99.9378 | 99.9349 |  | 0.041002 | 0.018139 | 32 | 8.3843 | 32 | 8.3843
11 | Tumkur | 6 | 6 | 12:55 | 128:05 | 109:06 | 70:35 | 179:41 | 192:36 | 32:06 | 99.8323 | 99.8202 | 2118:23 | 353:04 | 99.7785 | 99.7771 |  | 0.053821 | 0.043129 | 360 | 192.5933 | 60 | 32.0989
12 | Tiptur | 11 | 11 | 23:56 | 204:17 | 147:29 | 52:19 | 199:49 | 223:45 | 20:20 | 99.8983 | 99.8861 | 2749:31 | 249:57 | 99.8436 | 99.8422 |  | 0.054699 | 0.043884 | 490 | 223.75 | 44.5455 | 20.3409
13 | Madhugiri | 8 | 8 | 38:41 | 293:17 | 89:56 | 111:40 | 201:37 | 240:18 | 30:02 | 99.8589 | 99.8318 | 2443:57 | 305:30 | 99.8102 | 99.8071 |  | 0.048673 | 0.024641 | 261 | 240.3 | 32.625 | 30.0375
14 | Srinivaspura | 4 | 4 | 5:05 | 108:35 | 15:11 | 3:47 | 18:58 | 24:03 | 6:01 | 99.9734 | 99.9663 | 1336:04 | 334:01 | 99.7899 | 99.7891 |  | 0.18351 | 0.1772 | 153 | 24.05 | 38.25 | 6.0125
15 | KGF | 27 | 22 | 161:00 | 3998:38 | 123:00 | 427:00 | 550:00 | 711:00 | 26:20 | 99.8859 | 99.8525 | 17986:34 | 666:10 | 99.5832 | 99.5794 |  | 0.30272 | 0.27309 | 727 | 711 | 26.9259 | 26.3333
16 | CB Pura | 11 | 11 | 81:40 | 2150:06 | 232:42 | 127:21 | 360:03 | 441:43 | 40:09 | 99.8167 | 99.7751 | 5539:55 | 503:38 | 99.6867 | 99.6821 |  | 0.12995 | 0.093059 | 556 | 441.7167 | 50.5455 | 40.1561
17 | Chintamani | 13 | 13 | 54:58 | 755:53 | 200:20 | 66:55 | 267:15 | 322:13 | 24:47 | 99.8849 | 99.8612 | 12603:30 | 969:30 | 99.3906 | 99.3879 |  | 0.49426 | 0.47325 | 287 | 322.2167 | 22.0769 | 24.7859
18 | Devanahalli | 53 | 53 | 324:55 | 1742:19 | 1526:06 | 2567:15 | 4093:21 | 4418:16 | 83:22 | 99.5675 | 99.5331 | 1211.2715 | 548:30 | 99.6576 | 99.6537 | Devanahalli | -0.090127 | -0.12059 | 147 | 4418.2667 | 2.7736 | 83.3635
19 | Hosakote | 62 | 62 | 169:45 | 2471:36 | 1418:11 | 382:43 | 1800:54 | 1970:39 | 31:47 | 99.8373 | 99.822 | 22792:02 | 367:37 | 99.7696 | 99.7679 | Hosakote | 0.067678 | 0.054074 | 177 | 1970.65 | 2.8548 | 31.7847
20 | Nelamangala | 48 | 48 | 48:17 | 1295:16 | 568:47 | 440:26 | 1009:13 | 1057:30 | 22:02 | 99.8823 | 99.8766 | 15127:54 | 315:10 | 99.8017 | 99.801 | Nelamangala | 0.080583 | 0.075585 | 144 | 1057.5 | 3 | 22.0312
21 | Doddaballapura | 36 | 36 | 85:00 | 1176:41 | 511:20 | 859:50 | 1371:10 | 1456:10 | 40:27 | 99.7867 | 99.7735 | 11060:22 | 307:14 | 99.8075 | 99.806 | Doddaballapura | -0.020837 | -0.032569 | 64 | 1456.1667 | 1.7778 | 40.4491
22 | Bangalore south |  |  |  | 561:30 |  |  | 0:00 | 0:00 | #DIV/0! | #DIV/0! | #DIV/0! | 5735:07 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | #DIV/0! | #DIV/0! | 188
23 | Magadi |  |  |  | 197:38 |  |  | 0:00 | 0:00 | #DIV/0! | #DIV/0! | #DIV/0! | 12507:57 | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | #DIV/0! | #DIV/0!
22 | Magadi | 33 | 33 | 28:13 | 670:58 | 448:10 | 129:17 | 577:27 | 605:40 | 18:21 | 99.902 | 99.8972 | 8189:57 | 248:11 | 99.8439 | 99.8433 | Magadi | 0.058142 | 0.053894 | 219 | 605.6617 | 6.6364 | 18.3534
23 | Anekal | 127 | 127 | 4:35 | 290:50 | 2545:01 | 629:20 | 3174:21 | 3178:56 | 25:02 | 99.86 | 99.8598 | 23135:30 | 182:10 | 99.885 | 99.885 | Anekal | -0.024997 | -0.025177 | 3316 | 3178.9333 | 26.1102 | 25.031
24 | Ramanagara | 35 | 35 | 4:35 | 299:25 | 313:53 | 91:35 | 405:28 | 410:03 | 11:43 | 99.9351 | 99.9344 | 3630:10 | 103:43 | 99.9346 | 99.9345 | Ramanagara | 0.00051765 | -0.00013306 | 851 | 410.05 | 24.3143 | 11.7157
25 | Channapatna | 7 | 7 | 16:58 | 101:01 | 70:06 | 16:23 | 86:29 | 103:27 | 14:47 | 99.9308 | 99.9172 | 1572:13 | 224:36 | 99.8597 | 99.8582 | Channapatna | 0.071074 | 0.05903 | 301 | 103.45 | 43 | 14.7786
26 | Kanakapura | 22 | 22 | 9:35 | 123:37 | 148:06 | 30:27 | 178:33 | 188:08 | 8:33 | 99.9545 | 99.9521 | 3232:11 | 146:55 | 99.9075 | 99.9072 | Kanakapura | 0.047024 | 0.044859 | 320 | 188.1333 | 14.5455 | 8.5515
|  | 534 | 529 | 46.5468 | 14393:51 | 367.8513 | 254.0669 | 621.9182 | 668.465 | #DIV/0! | 99.8435 | 99.8317 | 6298.2726 | #DIV/0! | 99.8226 | 99.8213 | [6 empty] | 0
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month) | [22 empty] | #DIV/0!
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month) | [22 empty] | #DIV/0!
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [22 empty] | #DIV/0!
#DIV/0!
#DIV/0!
Note: In Devanahalli division, 2 feeders are newly added in month of Dec-17

## Dec ANX111
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
A. RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR DEC-2017 OF FY 2017-18
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cummulative Outage due to Incoming Supply Failure ( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Dec-2017 |  |  |  | Reliability for cummulative period From April-17 | [6 empty] | SAIFI & SAIDI of feeders for Dec-2017
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hr:mm:ss) | Outage duration per feeder (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers |  |  |  | Total No. of Feeders Interruption | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 |  |  |  | 17 | 18 | 19=17/3 | 20=18/3
1 | Davangere | 243 | 242 | 175:50 | 1570:05 | 5024:40 | 1320:14 | 6344:54 | 6520:44 | 26:50 | 99.805 | 99.7996 | 2886.1672 | 285:03 | 99.7607 | 99.7601 | 0.044363 | 0.039569 |  | 10351 | 6520.7333 | 42.5967 | 26.8343
2 | Harihara | 172 | 172 | 15:45 | 297:47 | 4345:38 | 1192:40 | 5538:18 | 5554:03 | 32:17 | 99.7596 | 99.7589 | 2833.7953 | 395:25 | 99.6672 | 99.6672 | 0.092325 | 0.091718 |  | 6308 | 5554.05 | 36.6744 | 32.291
3 | Chitradurga | 178 | 178 | 92:15 | 878:03 | 3626:24 | 3306:26 | 6932:50 | 7025:05 | 39:28 | 99.7092 | 99.7053 | 2316.3437 | 312:19 | 99.7375 | 99.7371 | -0.028378 | -0.031812 |  | 9086 | 7025.0833 | 51.0449 | 39.4668
4 | Hiriyur | 197 | 197 | 40:21 | 440:22 | 1993:20 | 763:38 | 2756:58 | 2797:19 | 14:12 | 99.8955 | 99.894 | 1739.8968 | 211:58 | 99.8217 | 99.8216 | 0.07375 | 0.072393 |  | 5404 | 2797.3094 | 27.4315 | 14.1995
5 | Tumkur | 385 | 385 | 68:00 | 814:53 | 3452:00 | 4856:00 | 8308:00 | 8376:00 | 21:45 | 99.8389 | 99.8375 | 4360.5537 | 271:50 | 99.7713 | 99.7712 | 0.067527 | 0.066356 | 0.047222 | 10151 | 8376 | 26.3662 | 21.7558
6 | Tiptur | 187 | 187 | 72:00 | 1020:21 | 2139:00 | 2789:00 | 4928:00 | 5000:00 | 26:44 | 99.8032 | 99.8003 | 2128.25 | 273:09 | 99.7704 | 99.7701 | 0.032814 | 0.030263 | 0.05 | 7856 | 5000 | 42.0107 | 26.738
7 | Madhugiri | 301 | 300 | 75:00 | 1160:32 | 4437:00 | 2410:00 | 6847:00 | 6922:00 | 23:00 | 99.8301 | 99.8283 | 3491.2133 | 278:22 | 99.7659 | 99.7657 | 0.064249 | 0.062598 | 0.052083 | 6953 | 6922 | 23.0997 | 22.9967
8 | Kolar | 143 | 143 | 61:02 | 215:42 | 2817:13 | 2979:05 | 5796:18 | 5857:20 | 40:58 | 99.6973 | 99.6941 | 9559:39 | 66:51 | 99.9441 | 99.9437 | -0.24676 | -0.24959 |  | 3481 | 5857.3306 | 24.3427 | 40.9604
9 | KGF | 187 | 133 | 756:00 | 15207:19 | 123:00 | 459:00 | 582:00 | 1338:00 | 7:09 | 99.9768 | 99.9466 | 1324.9951 | 170:03 | 99.8603 | 99.8569 | 0.1165 | 0.089714 | 0.525 | 1420 | 1338 | 7.5936 | 7.1551
10 | CB Pura | 188 | 188 | 753:50 | 1447.6618 | 3445:00 | 2797:07 | 6242:07 | 6995:57 | 37:13 | 99.7521 | 99.7221 | 3210.6014 | 409:52 | 99.6584 | 99.655 | 0.093698 | 0.067132 | 0.5235 | 10235 | 6995.95 | 54.4415 | 37.2125
11 | Chintamani | 141 | 141 | 85:00 | 12800:18 | 976:20 | 1479:30 | 2455:50 | 2540:50 | 18:01 | 99.8699 | 99.8654 | 2501.4472 | 425:47 | 99.6421 | 99.6416 | 0.22783 | 0.22384 |  | 1324 | 2540.8333 | 9.3901 | 18.0201
12 | Devanahalli | 34 | 34 | 238:55 | 1062:25 | 552:50 | 194:57 | 747:47 | 986:42 | 29:01 | 99.8358 | 99.7833 | 8561:53 | 251:49 | 99.7939 | 99.788 | 0.041825 | -0.0047312 |  | 86 | 986.7 | 2.5294 | 29.0206
13 | Hosakote | 32 | 32 | 50:10 | 1085:29 | 858:05 | 182:39 | 1040:44 | 1090:54 | 34:05 | 99.7571 | 99.7454 | 6315:40 | 197:22 | 99.8352 | 99.8339 | -0.078041 | -0.088428 |  | 66 | 1090.9 | 2.0625 | 34.0906
12 | Yelahanka | 66 | 66 | 289:05 | 2147:54 | 1410:55 | 377:36 | 1788:31 | 2077:36 | 31:29 | 99.7976 | 99.7649 | 14877:33 | 225:25 | 99.8139 | 99.8103 |  |  |  | 152 | 2077.6 | 2.303 | 31.4788
14 | Nelamangala | 14 | 14 | 15:48 | 316:57 | 70:32 | 31:35 | 102:07 | 117:55 | 8:25 | 99.9455 | 99.9371 | 2743:28 | 195:58 | 99.836 | 99.835 | 0.10954 | 0.10206 |  | 19 | 117.9167 | 1.3571 | 8.4226
15 | Doddaballapura | 35 | 35 | 132:45 | 946:16 | 211:40 | 316:50 | 528:30 | 661:15 | 18:54 | 99.8872 | 99.8589 | 7956:43 | 227:20 | 99.8118 | 99.8086 | 0.075413 | 0.050284 |  | 109 | 661.25 | 3.1143 | 18.8929
16 | Magadi | 42 | 42 | 23:30 | 358:36 | 191:35 | 280:55 | 472:30 | 496:00 | 11:49 | 99.916 | 99.9118 | 7980:23 | 190:01 | 99.8405 | 99.8401 | 0.075464 | 0.071757 |  | 1935 | 496 | 46.0714 | 11.8095
13 | Nelamangala | 91 | 91 | 172:03 | 1621:49 | 473:47 | 629:20 | 1103:07 | 1275:10 | 14:01 | 99.9095 | 99.8954 | 18680:34 | 205:17 | 99.8288 | 99.8272 |  |  |  | 2063 | 1275.1667 | 22.6703 | 14.0128
14 | Chandapura | 19 | 19 | 16:55 | 76:35 | 138:00 | 221:37 | 359:37 | 376:32 | 19:49 | 99.8587 | 99.852 | 2510:48 | 132:09 | 99.8895 | 99.8888 | -0.030846 | -0.036745 |  | 481.0486 | 376.5333 | 25.3183 | 19.8175
18 | Ramanagara | 39 | 39 | 32:59 | 181:43 | 1885:40 | 531:53 | 2417:33 | 2450:32 | 62:50 | 99.5371 | 99.5308 | 16399:51 | 420:31 | 99.6467 | 99.646 | -0.10963 | -0.11523 |  | 3363 | 2450.5333 | 86.2308 | 62.8342
19 | Channapatna | 47 | 47 | 36:38 | 783:04 | 620:32 | 303:38 | 924:10 | 960:48 | 20:27 | 99.8532 | 99.8474 | 8392:42 | 178:34 | 99.8503 | 99.8497 | 0.0028263 | -0.0023378 |  | 2637 | 960.8 | 56.1064 | 20.4426
15 | Ramanagara | 86 | 86 | 69:37 | 1002:19 | 2506:12 | 835:31 | 3341:43 | 3411:20 | 39:40 | 99.7098 | 99.7038 | 1034.5862 | 288:43 | 99.7576 | 99.757 |  |  |  | 6000 | 3411.3333 | 69.7674 | 39.6667
16 | Kanakapura | 64 | 64 | 10:44 | 97:08 | 1292:51 | 709:12 | 2002:03 | 2012:47 | 31:27 | 99.7664 | 99.7652 | 19810:00 | 309:32 | 99.7396 | 99.7395 | 0.02682 | 0.025708 |  | 776 | 2012.7833 | 12.125 | 31.4497
|  | 2344 | 2288 | 130.6603 | 3050.2299 | 1359.4529 | 987.7353 | 2347.1882 | 2477.8485 | 21.8171 | 99.8205 | 99.8106 | 22783.8318 | 208.4836 | 99.8048 | 99.8036 | 0.015784 |  |  |  |  | 0
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [16 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [16 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [16 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [16 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[15 empty] | 98.57 | 97.92 | -98.57 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[10 empty] | 265 | [6 empty] | 0 |  |  |  |  | #DIV/0!
[10 empty] | 88.3333 | [6 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
[17 empty] | 0 |  |  |  |  | #DIV/0!
Note: 1. In KGF division, 6 feeders were newly added. 2. In Chikkabalappura division, 1 feeder is newly added. 3. In Chinthamani division, 3 feeders were newly added. 4. In Hiriyur division, 2 feeeders were newly added
1. Newly added F13-NJY Handiganala of Sidlagatta USD sub-division of Sidlaghatta Muss.
2. Newly added F14-NJY Thummanahalli of Sidlagatta USD sub-division of Sidlaghatta.
3. Newly added F2-Saddahalli of Pallicherlu Muss of Sidlagatta RSD sub-division of Sidlaghatta.
4. Newly added F3-Marihalli of Pallicherlu Muss of Sidlagatta RSD sud-division of Sidlagatta.
5. Newly added F4-Chowdareddyhalli of Pallicherlu Muss of Sidlaghatta RSd sub-division of Sidlaghatta.